## Survey Summary Sheet
Big River Steel Galvanizing Line Motor PdMA Route 2023
Priority | Equipment Description | Motor I.D. Number | Electrical Condition | Corrected Mohm Value | Recommendation | Note
3 | AfterPOCoolingROT 1 | B40 0K020-1 | Within IEEE Standards | 1700 | Trend And Continue Testing
3 | AfterPOCoolingROT 2 | B40 0K020-2 | Within IEEE Standards | 20500 | Trend And Continue Testing
3 | AfterPOCoolingROT 3 | B40 0K020-3 | Within IEEE Standards | 20100 | Trend And Continue Testing
3 | AfterPOCoolingROT 4 | B40 0K020-4 | Within IEEE Standards | 14800 | Trend And Continue Testing
3 | BridleNo1DriveRoll1 | B20 FK001 | Within IEEE Standards | 16800 | Trend And Continue Testing
3 | BridleNo1DriveRoll2 | B20 FK021 | Within IEEE Standards | 15300 | Trend And Continue Testing
3 | BridleNo2DriveRoll1 | B40 KC001 | Within IEEE Standards | 17500 | Test Again In Six Months | Polar index is slighly low
3 | BridleNo2DriveRoll2 | B40 KC011 | Within IEEE Standards | 12000 | Trend And Continue Testing
3 | BridleNo3DriveRoll1 Exit Sec Bridle | B40 MC010 | Within IEEE Standards | 3800 | Trend And Continue Testing
3 | BridleNo3DriveRoll2 Exit Sec Bridle | B40 MC011 | Within IEEE Standards | 9800 | Trend And Continue Testing
3 | BridleNO4DriveRoll1 | B70 PD010 | Within IEEE Standards | 55300 | Trend And Continue Testing
3 | BridleNO4DriveRoll3 | B70 PD021 | Within IEEE Standards | 54500 | Trend And Continue Testing
3 | BridleNO4DriveRoll4 | B70 PD031 | Within IEEE Standards | 3100 | Test Again In Six Months | Polar index is slightly low
3 | BridleNO5DriveRoll1 | B70 RB001 | Within IEEE Standards | 13800 | Trend And Continue Testing
3 | BridleNO5DriveRoll2 | B70 RB011 | Within IEEE Standards | 5200 | Trend And Continue Testing
3 | BridleNO6DriveRoll1 | B70 RG001 | Within IEEE Standards | 30700 | Trend And Continue Testing
3 | BridleNO6DriveRoll2 | B70 RG011 | Within IEEE Standards | 41900 | Trend And Continue Testing | Check power leads from disconnect to motor
3 | BridleNO7DriveRoll1 | B70 TB001 | Within IEEE Standards | 22600 | Trend And Continue Testing
3 | BridleNO7DriveRoll2 | B70 TB011 | Within IEEE Standards | 19400 | Trend And Continue Testing
3 | BridleNO8DriveRoll1 | B90 UR001 | Within IEEE Standards | 4200 | Trend And Continue Testing | Check power leads from disconnect to motor
3 | BridleNO8DriveRoll2 | B90 UR011 | Within IEEE Standards | 7600 | Trend And Continue Testing
3 | Comb Air DFF | B40 LB020 | Within IEEE Standards | 32400 | Trend And Continue Testing
3 | Comb Air Post | B40 LB021 | Within IEEE Standards | 31300 | Trend And Continue Testing
3 | Comb Air RTF | B40 LB022 | Within IEEE Standards | 19600 | Trend And Continue Testing
3 | DryerAirBlowROT | B40 0P020 | Within IEEE Standards | 14000 | Trend And Continue Testing
3 | Entry Looper Winch Accumulator | B40 HE001 | Within IEEE Standards | 47000 | Trend And Continue Testing
3 | Exit Looper Winch Accumulator | B70 TF001 | Within IEEE Standards | 11100 | Trend And Continue Testing
3 | FinalPOTCoolingFanZone1 | B40 0M020-1 | Within IEEE Standards | 7200 | Trend And Continue Testing
3 | FinalPOTCoolingFanZone2 | B40 0M020-2 | Within IEEE Standards | 2200 | Trend And Continue Testing
3 | Fumes DFF Exhaust | B40 LC020 | Within IEEE Standards | 11100 | Trend And Continue Testing
3 | Fumes RTF Exhaust | B40 LC021 | Within IEEE Standards | 26500 | Trend And Continue Testing
3 | MillStandDriveBottom | B70 QA001-2 | Within IEEE Standards | 16900 | Trend And Continue Testing
3 | MillStandDriveTop | B70 QA001-1 | Within IEEE Standards | 1900 | Trend And Continue Testing
3 | Pay Off Drive Reel 1 | B20 CB001 | Within IEEE Standards | 7100 | Trend And Continue Testing
3 | Pay Off Drive Reel 2 | B20 DB001 | Within IEEE Standards | 11800 | Trend And Continue Testing
3 | SlowCoolingZone1 | B40 MA020-1 | Within IEEE Standards | 7300 | Trend And Continue Testing
3 | SlowCoolingZone2 | B40 MA020-2 | Within IEEE Standards | 9300 | Trend And Continue Testing
3 | Tension Reel | B90 WE001 | Within IEEE Standards | 4400 | Trend And Continue Testing
3 | Tension Reel #2 | B90 WQ001 | Within IEEE Standards | 4400 | Trend And Continue Testing
3 | UltraFACoolingROT 1 | B40 MB020-1 | Within IEEE Standards | 13500 | Trend And Continue Testing
3 | UltraFACoolingROT 2 | B40 MB020-2 | Within IEEE Standards | 9200 | Trend And Continue Testing
3 | UltraFACoolingROT 3 | B40 MB020-3 | Within IEEE Standards | 6500 | Trend And Continue Testing
3 | UltraFACoolingROT 4 | B40 MB020-4 | Within IEEE Standards | 8600 | Trend And Continue Testing

## After Pot Cooling OK020-J001
Summary

## After Pot Cooling OK020-J002
Summary

## After Pot Cooling OK020-J003
Summary

## After Pot Cooling OK020-J004
Summary

## BridleNo1DriveRoll1
Summary

## BridleNo1DriveRoll2
Summary

## BridleNo2DriveRoll1
Summary

## BridleNo2DriveRoll2
Summary

## BridleNo3DriveRoll1
Summary

## BridleNo4DriveRoll3
Summary

## BridleNo4DriveRoll4
Summary

## BridleNo5DriveRoll1
Summary

## BridleNo5DriveRoll2
Summary

## BridleNo6DriveRoll1
Summary

## BridleNo6DriveRoll2
Summary

## BridleNO7DriveRoll1
Summary

## BridleNO7DriveRoll2
Summary

## BridleNO8DriveRoll1
Summary

## BridleNO8DriveRoll2
Summary

## Comb Air DFF
Summary

## Comb Air Post
Summary

## Comb Air RTF
Summary

## DryerAirBlowROT
Summary

## Entry Looper Winch Accumulator
Summary

## Exit Looper Winch Accumulator
Summary

## FinalPOTCoolingFanZone1
Summary

## FinalPOTCoolingFanZone2
Summary

## Fumes DFF Exhaust
Summary

## Fumes RTF Exhaust
Summary

## MillStandDriveBottom
Summary

## MillStandDriveTop
Summary

## Pay Off Drive Reel 1
Summary

## Pay Off Drive Reel 2
Summary

## SlowCoolingZone1
Summary

## SlowCoolingZone2
Summary

## Tension Reel
Summary

## Tension Reel #2
Summary

## UltraFACoolingROT 1
Summary

## UltraFACoolingROT 2
Summary

## UltraFACoolingROT 3
Summary

## UltraFACoolingROT 4
Summary