|  |  |  |  |
| --- | --- | --- | --- |
| **Customer:** | NUCOR STEEL MEMPHIS INC.  | **Location/Desc:** | Memphis   |
| **Address:** | 3601 Paul R Lowry Road   | **Performed by:** | Kevin W Maxwell  |
|   | Memphis ,TN 38109   | **Date:** | 05/03/2023  |
| **Job/Order#** |   |   |   |

|  |  |
| --- | --- |
| **Reason for call:** | Field Balance   |
| **Description of work:** | Performed field balance on Combustion Air Fan #2. Balanced to . 5 mil pk-pkInitial imbalance 2.5 mil pk-pkWithin spec for 1775 rpm   |
| **Equipment and material used:** | 2 42 gram C Clamp weights   |
| **Recommended additional work:** |   |

|  |  |
| --- | --- |
| **Main Contact:** | Bryan Strozier  |
| **Customer Signature:** |   |

