|  |  |  |  |
| --- | --- | --- | --- |
| **Customer:** | ADM | **Location/Desc:** | MEMPHIS |
| **Address:** | 1795 DOCK ST | **Performed by:** | Kevin W Maxwell |
|  | MEMPHIS ,TN 38113 | **Date:** | 05/11/2023 |
| **Job/Order#** | 150139 |  |  |

|  |  |  |  |
| --- | --- | --- | --- |
| **Reason for call:** | Field balance | | |
| **Description of work:** | Found fan to be rubbing against inner cone. Adjusted fan and realigned sheaves and set belt tension. Performed field balance on fan. Initial imbalance 1.2 mil pk-pk. Final imbalance .3 mil pk-pk. Within spec for 2300 rpm. | | |
| **Equipment and material used:** | 2 15 gram C clamp weights | | |
| **Recommended additional work:** |  | | |

|  |  |  |  |
| --- | --- | --- | --- |
| **Main Contact:** | Trent Lebon | | |
| **Customer Signature:** |  | | |

