|  |  |  |  |
| --- | --- | --- | --- |
| **Customer:** | ADM  | **Location/Desc:** | MEMPHIS   |
| **Address:** | 1795 DOCK ST   | **Performed by:** | Kevin W Maxwell  |
|   | MEMPHIS ,TN 38113   | **Date:** | 05/11/2023  |
| **Job/Order#** | 150139  |   |   |

|  |  |
| --- | --- |
| **Reason for call:** | Field balance   |
| **Description of work:** | Found fan to be rubbing against inner cone. Adjusted fan and realigned sheaves and set belt tension. Performed field balance on fan. Initial imbalance 1.2 mil pk-pk. Final imbalance .3 mil pk-pk. Within spec for 2300 rpm.   |
| **Equipment and material used:** | 2 15 gram C clamp weights   |
| **Recommended additional work:** |   |

|  |  |
| --- | --- |
| **Main Contact:** | Trent Lebon  |
| **Customer Signature:** |   |

