|  |  |  |  |
| --- | --- | --- | --- |
| **Customer:** | BIO ENERGY DEVELOPMENT | **Location/Desc:** | Memphis |
| **Address:** | 2227 Deadrick Ave | **Performed by:** | Kevin W Maxwell |
|  | Memphis ,TN 38114 | **Date:** | 05/15/2023 |
| **Job/Order#** | 149094 |  |  |

|  |  |  |  |
| --- | --- | --- | --- |
| **Reason for call:** | Vibration analysis on Chiller | | |
| **Description of work:** | Performed vibration analysis on Chiller 1 Motor and Compressor.  Found vibrations to be low.  Outboard motor bearing temp is higher than normal on both motors. 180-190F on OB and 123 F on IB motor bearings. | | |
| **Equipment and material used:** |  | | |
| **Recommended additional work:** |  | | |

|  |  |  |  |
| --- | --- | --- | --- |
| **Main Contact:** | Tracy Irving | | |
| **Customer Signature:** |  | | |