|  |  |  |  |
| --- | --- | --- | --- |
| **Customer:** | BIO ENERGY DEVELOPMENT  | **Location/Desc:** | Memphis   |
| **Address:** | 2227 Deadrick Ave   | **Performed by:** | Kevin W Maxwell  |
|   | Memphis ,TN 38114   | **Date:** | 05/15/2023  |
| **Job/Order#** | 149094  |   |   |

|  |  |
| --- | --- |
| **Reason for call:** | Vibration analysis on Chiller   |
| **Description of work:** | Performed vibration analysis on Chiller 1 Motor and Compressor. Found vibrations to be low. Outboard motor bearing temp is higher than normal on both motors. 180-190F on OB and 123 F on IB motor bearings.   |
| **Equipment and material used:** |   |
| **Recommended additional work:** |   |

|  |  |
| --- | --- |
| **Main Contact:** | Tracy Irving  |
| **Customer Signature:** |   |