|  |  |  |  |
| --- | --- | --- | --- |
| **Customer:** | NUCOR STEEL MEMPHIS INC.  | **Location/Desc:** | Memphis   |
| **Address:** | 3601 Paul R Lowry Road   | **Performed by:** | Kevin W Maxwell  |
|   | Memphis ,TN 38109   | **Date:** | 08/16/2023  |
| **Job/Order#** |   |   |   |

|  |  |
| --- | --- |
| **Reason for call:** | Field Balance   |
| **Description of work:** | Performed field balance on Torch Cooling Fan. Fan is resonant but we were able to lower vibration from 20 mils to 4 mils.   |
| **Equipment and material used:** | 4 air foil clips   |
| **Recommended additional work:** |   |

|  |  |
| --- | --- |
| **Main Contact:** | chris Clements  |
| **Customer Signature:** |   |