Date: 05/28/2019

Xylem
Account:
Operation:
Attention: Kevin piper
Reference: Job#139807 Direct Drive

Kevin piper,

Upon completing a full evaluation on xx/yy/zz, the following was found:
Winding
Phase to phase the paper was too short which allowed the two phases too touch each other
Rewind an bearings

Please find attached, all supporting documentation along images of discovery found during the teardown & inspection of this evaluation. Should you have any questions or require further assistance with this matter, please contact us.

Our estimate for repair of the apparatus is attached as a supplementary document.

Sincerely,

Andrew Skala
Senior Motor Shop Coordinator & Electrical Engineer