## Vibration Matrix New
Monthly Memphis Asset Health Report Equipment Report | [66 empty] | total |  | done | %
Emergency -1 | SAP Emergency Priority 1 - Class IV; Defect (s) present that makes continued reliability unpredictable, and possibility of secondary damage is high. Repairs should be made ASAP. An unscheduled shutdown should be considered for repairsmmediate action required. <24 hours |  |  |  |  | 1% | 0% | 0% | 0% | 0.2488% | 0.995% | 0.2488% | 0.2488% | 0% | 0.5155% | 1.081% | 0.995% | 1.493% | 0.4975% | 1.99% | 1.068% | 1.244% | 3.234% | 1.741% | 1.493% | 2.239% | 3.234% | [15 empty] | 0.53556 | [23 empty] | 189 | north | 112 | 59.26%
Urgent -2 | SAP Urgent Priority 2 - Class III; Defect (s) present that may cause failure in short term (less than 2 months.). This should be addressed as soon as practical, with a high maintenance priority. Increase monitoring frequency. |  |  |  |  | 2% | 0.2232% | 0.9639% | 1.79% | 1.79% | 2.046% | 0.5115% | 1.279% | 0% | 2.835% | 2.703% | 5.371% | 7.417% | 9.207% | 9.207% | 6.41% | 7.673% | 8.696% | 7.417% | 8.184% | 5.882% | 5.115% | [37 empty] | 6.375 |  | 245 | south | 215 | 87.76%
Routine -3 | SAP Priority 3 - Class II: Defect (s) present that may cause problem in long term (2-6 months.). Repair during normal maintenance scheduling. Continue to monitor. |  |  |  |  | 3% | 0% | 1.687% | 3.325% | 4.604% | 5.115% | 2.302% | 2.813% | 0% | 5.67% | 11.89% | 16.37% | 15.6% | 17.14% | 15.09% | 14.74% | 14.32% | 16.37% | 11.51% | 11.51% | 11.76% | 3.581% | [41 empty] | 67
Watch -4 | Low level event has been noticed on this machine. No immediate action is required. Informational purposes only. |  |  |  |  | 4% | 0.2232% | 0.241% | 5.882% | 4.604% | 5.115% | 1.79% | 0.5115% | 0% | 3.351% | 5.135% | 7.417% | 7.673% | 8.696% | 6.65% | 3.205% | 6.65% | 6.65% | 6.65% | 6.394% | 3.325% | 2.046% | [39 empty] | 434 |  | 327 | 0.75346
Condition is acceptable - OK | Machinery condition acceptable. |  |  |  |  | OK% | 39.29% | 66.75% | 55.75% | 68.8% | 68.29% | 44.5% | 47.83% | 9.974% | 45.62% | 65.14% | 55.5% | 54.48% | 49.1% | 41.18% | 46.37% | 51.92% | 61.13% | 55.24% | 54.99% | 58.31% | 38.87%
Not tested this survey - NR | Machinery not in operation or out of service. |  |  |  |  | NR% | 62.5% | 40.72% | 50.38% | 37.08% | 33.5% | 64.71% | 65.73% | 108.2% | 61.34% | 39.19% | 32.74% | 31.71% | 33.25% | 43.99% | 26.92% | 35.55% | 20.46% | 27.37% | 32.99% | 29.92% | 23.53%
Waiting Analyst Ranking - WR | [5 empty] | Total | 39.73% | 69.64% | 66.75% | 80.04% | 81.56% | 49.35% | 52.68% | 9.974% | 58.25% | 85.68% | 90.98% | 92.92% | 90.74% | 79.02% | 77.24% | 75.59% | 90.8% | 85.44% | 78.4% | 83.45% | 84.91% | 16.55%
SAP | SAP Description | Route | New Number | New Description | comments | Route | 2020-04-01 | 2020-05-01 | 2020-06-01 | 2020-07-01 | 2020-08-01 | 2020-09-01 | 2020-10-01 | 2020-11-01 | 2020-12-01 | 2021-01-01 | 2021-02-01 | 2021-03-01 | 2021-04-01 | 2021-05-01 | 2021-06-01 | 2021-07-01 | 2021-08-01 | 2021-09-01 | 2021-10-01 | 2021-11-01 | 2021-12-21 | 2022-01-22 | Dave Shook | Dave Shook- Comments | Kevin Maxwell | Kevin Maxwell - Comments | Comments | SAP WO# | Date created | Last Reading | Lessons Learned | Before or after | Best Case Loss Hours | Points |  | greaseable ? | Oil Sample Data | Picture | Motor Speed (rpm) | Motor IB bearing | Motor OB Bearing | VFD | Motor HP | Motor Frame Size | Motor Sheave Diameter | Fan RPM | Fan Bldes | Fan Sheave Diameter | Fan Bearings | Type of Belts Used | New Belt Tension | Used Belt Tension | Coupling | Pump Type | Impellor vanes | Gear teeth | Comments | [6 empty] | n | 19
MEM-PRO-010-UTL-IAS-0820 | MSS-N PLANT #3 AIR COMPRESSOR 100 HP | North Util | 10-0820 | #3 AIR COMPRESSOR 100 HP |  | North | NR | OK | OK | OK | OK | OK | OK | NR | OK | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | NR |  |  | 3 | Overall acceleration has increased this survey in the motor. Motor data still shows harmonics of the driven shaft (faster screw comp. shaft) of the air end. This motor does have some higher amplitudes than the other compressors; therefore, it is recommended to collect trend able vibration data on the compressor and inspect the compressor as time allows. | Overall acceleration has increased this survey in the motor. Motor data still shows harmonics of the driven shaft (faster screw comp. shaft) of the air end. This motor does have some higher amplitudes than the other compressors; therefore, it is recommended to collect trend able vibration data on the compressor and inspect the compressor as time allows. Rated as a CLASS II defect. | 7231191 | #VALUE! | 2021-12-14 |  |  |  | 8 | 32
MEM-PRO-010-UTL-IAS-0890 | MSS-N PLANT #4 AIR COMPRESSOR 200 HP | North Util | 10-0890 | #4 AIR COMPRESSOR 200 HP |  | North | NR | OK | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | OK | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 37
MEM-PRO-010-UTL-IAS-0891 | MSS-N PLANT #5 AIR COMPRESSOR 150 HP | North Util | 10-0891 | #5 AIR COMPRESSOR 150 HP |  | North | NR | OK | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | NR | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 4
MEM-PRO-010-UTL-IAS-1401 | MSS-#6 200 HP AIR COMPRESSOR | North Util | 10-1401 | #6 200 HP AIR COMPRESSOR |  | North | NR | OK | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | OK | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 6
MEM-PRO-010-UTL-IAS-2100 | MSS-N PLANT #2 AIR COMPRESSOR 125 HP | North Util | 10-2100-0 | #2 AIR COMPRESSOR 125 HP |  | North | NR | OK | OK | NR | NR | NR | NR | NR | NR | NR | ok | NR | NR | ok | NR | NR | ok | NR | NR | NR | NR | NR |  |  | OK |  | decreased. Check and inspect the unit fasteners, coupling, alignment, and base. |  |  | 2021-08-30
MEM-PRO-010-UTL-PRW-2495 | MN-PLT STH 90 DEG WTR TK S. SUPPLY PUMP | North Util | 10-2495-0 | 90 D WTR TK S SUPPLY PUMP #3 |  | North | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | ok | NR | NR | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14
MEM-PRO-010-UTL-PRW-2496 | MSS-MN PLT NORTH 90 DEG WTR TK N PUMP | North Util | 10-2496-0 | 90 D WTR TK N SUPPLY PUMP #1 |  | North | NR | NR | OK | OK | OK | OK | OK | NR | NR | OK | ok | OK | OK | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14
MEM-PRO-010-UTL-IAS-4141 | 800 Ton 2P 60HP AIR COMPRESSOR | 800 Ton | 10-4141-0 | 800T 2P 60HP AIR COMPRESSOR |  | South | NR | OK | NR | OK | OK | ok | NR | NR | NR | OK | OK | OK | OK | ok | ok | ok | ok | ok | ok | ok | NR | NR | [7 empty] | 2021-11-17
MEM-PRO-010-UTL-IAS-4142 | MSS-800T 100 HP CTR AIR COMPRESSOR | 800 Ton | 10-4142-0 | 800T 100 HP AIR COMPRESSOR |  | South | NR | OK | NR | OK | OK | ok | OK | NR | NR | OK | ok | 1 | 3 | 2 | NR | 4 | 4 | 4 | 4 | 4 | 4 | NR |  |  |  |  | Same. No action required. |  |  | 2021-12-21 |  |  |  | 16 | 49
MEM-PRO-014-GRD-MFG-3008 | MSP-GRINDER SURGE BIN ASP. FAN | 800 Ton | 14-3008 | GRINDER SURGE BIN ASP FAN |  | South | NR | 3 | 3 | 2 | 2 | OK | OK | NR | NR | OK | OK | OK | OK | 4 | 3 | ok | ok | ok | 4 | ok | ok | NR | [7 empty] | 2021-12-21 | #N/A |  |  | 16 | 4 | [6 empty] | Yes
MEM-PRO-014-GRD-MFG-3016 | MSP-N FLAKE GRINDING MILL | 800 Ton | 14-3016 | MSP-N FLAKE GRINDING MILL |  | South | NR | OK | NR | OK | OK | OK | OK | NR | NR | 4 | OK | OK | 3 | 3 | OK | 3 | 3 | 4 | 4 | 4 | NR | NR |  |  |  |  | Motor and fan speed vibrations in multiple points. Inspect the unit for wear and alignment in the drive train components. Inboard grinder bearing data shows possible early bearing defect frequencies. Inspect the grinder bearings as time allows. Rated a Class II Defect. |  |  | 2021-11-17 |  |  |  | 16 | 28
MEM-PRO-014-GRD-MFG-3029 | MSP-S. FLAKE GRINDING MILL | 800 Ton | 14-3029 | MSP-S FLAKE GRINDING MILL |  | South | NR | OK | NR | OK | OK | OK | OK | NR | NR | 4 | OK | 4 | 3 | 3 | OK | 4 | 4 | 4 | 4 | 4 | 4 | NR |  |  |  |  | Motor speed vibration. Inspect as time allows. |  |  | 2021-12-21 |  |  |  | 16 | 4 | [6 empty] | Yes
MEM-PRO-014-GRD-MFG-3043 | MSP-N. DUST COLLECTOR ASP FAN #1 | 800 Ton | 14-3043 | N DUST COLLECTOR ASP FAN #1 |  | South | NR | OK | NR | OK | OK | OK | OK | OK | NR | OK | ok | 4 | 4 | NR | 3 | 3 | ok | ok | ok | ok | 3 | NR |  |  |  |  | Jump in vibration. Inspect drive train. Confirm all shaft speeds. | 7277493 |  | 2021-12-21 |  |  |  | 16 | 4
MEM-PRO-014-GRD-MFG-3048 | MSP-S. DUST COLLECTOR ASP FAN #2 | 800 Ton | 14-3048 | S DUST COLLECTOR ASP FAN #2 |  | South | NR | 3 | NR | OK | OK | OK | OK | NR | NR | OK | ok | OK | OK | ok | OK | OK | OK | OK | OK | OK | 3 | NR |  |  |  |  | Jump in vibration. Inspect drive train. Confirm all shaft speeds. | 7277494 |  | 2021-12-21 | #N/A |  |  | 16 | 33
MEM-PRO-014-UTL-IAS-4120 | MSP-40 HP S 800T AIR COMPRESSOR | 800 Ton | 14-4120 | 40 HP S 800T AIR COMPRESSOR |  | South | NR | OK | NR | OK | OK | OK | OK | NR | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | NR | [7 empty] | 2021-12-21 |  |  |  | 8 | 6
MEM-PRO-015-GRD-M2G-3008 | MS2P-GRINDER SURGE BIN FLTR RCVR ASP FAN | 800 Ton | 15-3008 | GRINDER SURGE BIN FLTR FAN |  | South | NR | OK | NR | NR | NR | ok | NR | NR | NR | NR | 4 | 4 | 4 | ok | NR | ok | ok | ok | ok | ok | ok | NR |  |  |  |  | 1x and 2x RPM fan speed vibrations still in the motor. Inspect the drive train components for wear, eccentricity, runout, and alignment. Rated a Class I Defect. |  |  | 2021-12-21 |  |  | 4 | 8 | 3
MEM-PRO-015-GRD-M2G-3016 | MS2P-N FLAKE GRINDING MILL | 800 Ton | 15-3016 | MS2P-N FLAKE GRINDING MILL |  | South | NR | OK | NR | OK | OK | ok | OK | NR | NR | OK | OK | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | NR |  |  |  |  | motor and fan base structural defects, shaft or sheave run out, sheave alignment, belt tension, and |  |  | 2021-12-21 |  |  |  | 24 | 6
MEM-PRO-015-GRD-M2G-3029 | MS2P-S FLAKE GRINDING MILL | 800 Ton | 15-3029 | MS2P-S FLAKE GRINDING MILL |  | South | NR | OK | NR | OK | OK | ok | OK | NR | NR | OK | 4 | 3 | 4 | NR | OK | 4 | 3 | ok | ok | ok | NR | NR |  |  |  |  | build up or damage on the fan wheel. Check for proper air flow parameters. Trim balancing might be |  |  | 2021-11-17 |  |  |  | 16 | 6
MEM-PRO-015-GRD-M2G-3034 | MS2P-GROUND FLAKE TRANSFER BLOWER | 800 Ton | 15-3034 | GROUND FLAKE TRANSFER BLOWER |  | South | NR | OK | 3 | NR | 3 | WR | OK | NR | NR | OK | OK | 4 | NR | 3 | 4 | 4 | 3 | ok | ok | ok | ok | NR |  |  |  |  | needed. Rated a Class II Defect. |  |  | 2021-12-21 | #N/A |  |  | 16 | 6
MEM-PRO-015-GRD-M2G-3043 | MS2P-N GRIND MILL RECEIVER ASP FAN | 800 Ton | 15-3043 | N GRIND MILL RECEIVE ASP FAN |  | South | NR | OK | NR | OK | OK | ok | OK | NR | NR | OK | 3 | 3 | 3 | 2 | 3 | 2 | 1 | 2 | 2 | 2 | ok | NR |  |  |  |  | Vibration data shows another increase in fan speed vibration amplitude in the motor and fan. Motor is higher. Inspect the unit for loose fasteners, structural defects, sheave alignment, belt tension, and build up or damage on the fan wheel. Trim balancing will be needed, or fan wheel replaced. Rated a Class IV Defect | 7268983 | #VALUE! | 2021-12-21 |  |  | 1 | 16 | 6
MEM-PRO-015-GRD-M2G-3048 | MS2P-S GRIND MILL RECEIVER ASP FAN | 800 Ton | 15-3048 | S GRIND MILL RECEIVE ASP FAN |  | South | NR | OK | 3 | 2 | 2 | WR | OK | ok | NR | OK | OK | OK | 3 | 1 | 3 | 2 | 2 | 2 | 3 | 2 | ok | NR |  |  |  |  | Data still shows a strong fan speed vibration in the motor vertical. Inspect the unit for loose fasteners, | 7260027 | #VALUE! | 2021-12-21 |  |  | 1 | 16 | 3
MEM-PRO-022-UNL-TK1-0604 | MSS-N FLAKE BLOWER @ TRACK #1 | 800 Ton | 22-0604 | N FLAKE BLOWER @ TRACK #1 |  | South | NR | NR | NR | 3 | 3 | WR | OK | NR | NR | 3 | 3 | 3 | 2 | 3 | 3 | 3 | 1 | ok | 2 | 2 | 3 | NR |  |  |  |  | Check drivetrain components for wear and alignment. | 7228135 | #VALUE! | 2021-12-21 |  |  |  | 16 | 3
MEM-PRO-022-UNL-TK1-0614 | MSS-S FLAKE BLOWER @ TRACK #1 | 800 Ton | 22-0614 | S FLAKE BLOWER @ TRACK #1 |  | South | NR | NR | OK | 3 | 2 | WR | OK | NR | NR | OK | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | ok | 3 | NR |  |  |  |  | Motor inboard vertical has increased. Inspect fasteners and drive train components. | 7277495 |  | 2021-12-21 |  |  |  | 16 | 3
MEM-PRO-022-UNL-TK1-0687 | MSS-TRACK 1 VACUUM BLOWER | 800 Ton | 22-0687 | TRACK 1 VACUUM ASP BLOWER |  | South | NR | NR | NR | OK | OK | ok | OK | NR | NR | 3 | NR | 1 | 3 | 3 | NR | NR | 4 | NR | NR | ok | 4 | NR |  |  |  |  | Motor axial is up. Check drivetrain for wear and alignment. |  |  | 2021-12-21 |  |  |  | 16 | 6
MEM-PRO-022-UNL-TK5-2040 | MSS-CYCLONAIRE EAST RAIL UNLOAD SYS | 800 Ton | 22-2040 | TRACK 5 BLOWER |  | South | NR | OK | NR | OK | OK | ok | OK | NR | NR | 3 | 3 | 3 | 4 | 4 | 4 | NR | ok | ok | ok | ok | 4 | NR |  |  |  |  | Motor axial is up. Check drivetrain for wear and alignment |  |  | 2021-12-21 |  |  |  | 8 | 6
MEM-PRO-022-STS-C8T-5028 | CENTER 800T BIN BLOWER | 800 Ton | 22-5028 | C 800T BIN DISCHARGE BLOWER |  | South | NR | NR | NR | NR | OK | NR | NR | NR | NR | OK | OK | OK | OK | ok | NR | ok | ok | ok | ok | ok | ok | NR | [7 empty] | 2021-12-21 |  |  |  | 16 | 6
MEM-PRO-022-STS-W8T-5031 | MSS-WEST 800T TRANSFER BLOWER | 800 Ton | 22-5031 | W 800T TRANSFER DIS BLOWER |  | South | NR | NR | NR | OK | NR | NR | NR | NR | NR | NR | NR | 2 | NR | ok | NR | NR | 3 | bad data | bad data | NR | 3 | NR |  |  |  |  | Motor 1x RPM is up especially in axial. Bearings show defects also but could be due to higx axial velocity. Check drive train for wear and alignment. Ensure bearings are lubricated. Watch motor bearings after maintenance. | 7237521 | #VALUE! | 2021-12-21 |  |  |  | 8 | 6 | [24 empty] | fan and bearings replaced 5/27
MEM-PRO-022-STS-E8T-5032 | MSS-E 800T BIN TRANSFER BLOWER | 800 Ton | 22-5032 | E 800T BIN TRANS DIS BLOWER |  | South | NR | NR | NR | NR | 3 | WR | OK | NR | NR | OK | OK | NR | OK | NR | OK | 3 | W-R | ok | ok | ok | NR | NR |  |  |  |  | Apparent blower harmonic vibrations in the motor. Please confirm shaft speeds to help identify issues. Inspect the unit fasteners and drive train components for defects and alignment. Rated a Class II Defect. |  |  | 2021-11-17 |  |  |  | 8 | 6
MEM-PRO-015-WEI-WIS-3050 | MSP-FLAKE BIN EXHAUST FAN | MS2P Curd | 15-3050 | FLAKE BIN EXHAUST FAN |  | South | NR | 2 | 2 | OK | WR | NR | NR | NR | OK | OK | 4 | OK |  | ok | 4 | 4 | 3 | 3 | 3 | 3 | 3 | WR |  |  |  |  | Fan bearings still shows lower frequency range shaft speed harmonic and non-synchronous vibrations. Inspect the unit fan bearings for looseness. Bearings could be in distress. Check drive train components for wear and alignment. Ensure all fasteners are tight. Check for structural or fasteners issues. Rated a Class II Defect. | 7258996 | #VALUE! | 2022-01-13 |  |  | 4 | 16 | 6
MEM-PRO-015-WEI-WIS-3085 | MS2P-WET-IN FLAKE SCREW CONVEYOR | MS2P Curd | 15-3085 | WET-IN FLAKE SCREW CONVEYOR | RPM | South | NR | OK | OK | OK | OK | NR | NR | NR | OK | OK | OK | OK | OK | ok | OK | 4 | 4 | 4 | 4 | ok | ok | WR |  |  |  |  | Motor still shows a slight increase in a vibration at 31.8 Hz. Please confirm motor RPM. Check all fasteners, coupling and alignment as time allows. Rated a Class I Defect. |  |  | 2022-01-13 |  |  | 4 | 16 | 6
MEM-PRO-015-WEI-WIS-3090 | MS2P-WET IN TRANSFER PUMP | MS2P Curd | 15-3090 | MS2P-WET IN TRANSFER PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | 3 | OK | OK | OK | OK | OK | OK | 4 | WR |  |  |  |  | Possible electrical vibration in the motor due to a peak at near 360 Hz. Check drive if equipped and electrical connections and shaft alignment due to a 2x RPM vibration. |  |  | 2022-01-13 |  |  | 4 | 16 | 6
MEM-PRO-015-XTR-1EX-3114 | MS2P-1ST EXTRACTION TANK FEED PUMP | MS2P Curd | 15-3114 | 1ST EXT TANK FEED PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | WR | 4 | WR |  |  |  |  | Possible electrical vibration in the motor due to a peak at near 360 Hz. Check drive if equipped and electrical connections. |  |  | 2022-01-13 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-XTR-2EX-3130 | MEM-PRO-015-XTR-2EX-3130 | MS2P Curd | 15-3130 | 2ND EXTRACTION FEED PUMP |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | OK | OK | OK | ok | ok | ok | WR | [7 empty] | 2022-01-13 |  |  | 6 | 24 | 6
MEM-PRO-015-XTR-1EX-3133 | MS2P-#9 CENTRIFUGE DEFOAMER PUMP | MS2P Curd | 15-3133 | #9 CENTRIFUGE DEFOAMER PUMP | not running | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | 4 | 3 | 4 | 3 | bad data | 4 | 4 | 4 | WR |  |  |  |  | Check all fasteners, coupling and alignment. |  |  | 2022-01-13 |  |  |  | 24 | 6
MEM-PRO-015-XTR-1EX-3137 | MS2P-#8 CENTRIFUGE DEFOAMER PUMP | MS2P Curd | 15-3137 | #8 CENTRIFUGE DEFOAMER PUMP |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | bad data | ok | ok | 4 | WR |  |  |  |  | Check all fasteners, coupling and alignment. |  |  | 2022-01-13 |  |  | 6 | 16 | 6
MEM-PRO-015-XTR-1EX-3141 | MS2P-#9 1ST EXTRACTION CENTRIFUGE | MS2P Curd | 15-3141 | #9 1ST EXT SHARPLE CENTRIFUG |  | South | NR | OK | 2 | 2 | 2 | NR | 3 | NR | OK | OK | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 4 | 2 | 2 | 4 | WR |  |  |  |  | Clean and flush. | flush |  | 2022-01-13 |  |  |  | 12 | 6
MEM-PRO-015-XTR-1EX-3141 | MS2P-#9 1ST EXTRACTION CENTRIFUGE | MS2P Curd | 15-3141-08 | #9 1ST EXT CENTRIFUGE OIL P |  | South | NR | 3 | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | ok | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-XTR-2EX-3149 | MS2P-#6 2ND EXTRACTION CENTRIFUGE | MS2P Curd | 15-3149 | #6 2ND EXT CENT SHARPLES |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | ok | ok | 2 | WR |  |  |  |  | The centrifuge inboard bearing still shows a strong shaft speed vibration and a few harmonics indicating possible looseness. The unit should be cleaned and flushed. The shaft could have some run out, check with a dial indicator. B1V measurement has also significantly increased at centrifuge speed. Check the bearing fasteners and sheave alignment. | flush |  | 2022-01-13 |  |  | 1 | 16 | 6
MEM-PRO-015-XTR-2EX-3149 | MS2P-#6 2ND EXTRACTION CENTRIFUGE | MS2P Curd | 15-3149-08 | #6 2ND EXT CENTRIFUGE OIL P |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | ok | wr | 3 | WR |  |  |  |  | Kevin you cant flush oil pump | fluch |  | 2022-01-13 |  |  | 1 | 27 | 6 |  | drain sample with online filtering and oil coolier | [7 empty] | 18" 10 5V1800 PP5811 | 3050 |  | 10 1/2" PP5785 |  | 10ea 18" 5VX1800 PP1338 | 7 to 8 lbf | 6 to 7 lbf
MEM-PRO-015-XTR-1EX-3151 | MS2P-#8 1ST EXTRACTION CENTRIFUGE | MS2P Curd | 15-3151 | #8 1ST EXT CENT SHARPLES |  | South | NR | OK | 4 | OK | OK | NR | 3 | NR | OK | 4 | 3 | 3 | 3 | 2 | 4 | 3 | 3 | 3 | 3 | 3 | 4 | WR |  |  |  |  | Vibration data for the motor still shows non-synchronous vibrations in the bearings. We believe the bearing are in some distress. Ensure the bearings are lubricated properly if applicable. Clean and flush. | 7257552 | #VALUE! | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-XTR-1EX-3151 | MS2P-#8 1ST EXTRACTION CENTRIFUGE | MS2P Curd | 15-3151-08 | #8 1ST EXT CENTRIFUGE OIL P |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | ok | ok | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 28 | 6 |  | drain sample with online filtering and oil coolier | [7 empty] | 18" 10 5V1800 PP5811 | 3050 |  | 10 1/2" PP5785 |  | 10ea 18" 5VX1800 PP1338 | 7 to 8 lbf | 6 to 7 lbf
MEM-PRO-015-CLG-CLF-3156 | MS2P-CLARIFIER FEED BOOSTER PUMP | MS2P Curd | 15-3156 | CLARIFIED FEED BOOSTER PUMP |  | South | NR | OK | OK | OK | OK | NR | NR | NR | OK | OK | 3 | 3 | 3 | 4 | OK | OK | OK | OK | ok | ok | ok | WR |  |  |  |  | The motor bearings are still in some distress and have been for a while. The overall acceleration is just below 2 g’s again this survey. We will watch this unit for changes. Expect to change the motor sometime in the future. Rated a Class II Defect. |  |  | 2022-01-13 |  |  | 6 | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-XTR-1EX-3161 | MS2P-#7 1ST EXTRACTION CENTRIFUGE | MS2P Curd | 15-3161 | #7 1ST EXT CENT SHARPLES |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | 4 | 4 | 2 | 2 | 3 | 3 | 3 | 3 | wr | 4 | WR |  |  |  |  | 1x, 2x at C1V CHECK ALIGNMENT, CLEAN AND FLUSH | 7274535 |  | 2022-01-13 |  |  |  | 27 | 6 |  | drain sample with online filtering and oil coolier | [7 empty] | 18" 10 5V1800 PP5811 | 3050 |  | 10 1/2" PP5785 |  | 10ea 18" 5VX1800 PP1338 | 7 to 8 lbf | 6 to 7 lbf
MEM-PRO-015-XTR-1EX-3161 | MS2P-#7 1ST EXTRACTION CENTRIFUGE | MS2P Curd | 15-3161-08 | #7 1ST EXT CENTRIFUGE OIL P |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | ok | ok | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-XTR-3EX-3171 | MS2P-#5 3RD EXTRACTION CENTRIFUGE | MS2P Curd | 15-3171 | #5 3RD EXT CENT SHARPLES |  | South | NR | OK | 4 | 4 | WR | NR | OK | NR | OK | OK | 3 | 4 | OK | 4 | OK | OK | OK | OK | ok | wr | 4 | WR |  |  |  |  | Motor 1x RPM vibration is up. Check all fasteners as well as sheave run out and alignment. INCREASE IN 2X IN C2A, CHECK ALIGNMENT | 7274537 |  | 2022-01-13 |  |  | 1 | 27 | 6 |  | drain sample with online filtering and oil coolier | [7 empty] | 18" 10 5V1800 PP5811 | 3050 |  | 10 1/2" PP5785 |  | 10ea 18" 5VX1800 PP1338 | 7 to 8 lbf | 6 to 7 lbf
MEM-PRO-015-XTR-3EX-3171 | MS2P-#5 3RD EXTRACTION CENTRIFUGE | MS2P Curd | 15-3171-08 | #5 3RD EXT CENTRIFUGE OIL P |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | ok | ok | ok | WR | [7 empty] | 2022-01-13 |  |  | 1 | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-XTR-2EX-3179 | MS2P-#6 CENTRIFUGE DEFOAMER PUMP | MS2P Curd | 15-3179 | #6 CENTRIFUGE DEFOAMER PUMP |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | bad data | ok | ok | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-XTR-1EX-3207 | MS2P-#7 CENTRIFUGE DEFOAMER PUMP | MS2P Curd | 15-3207 | #7 CENTRIFUGE DEFOAMER PUMP |  | South | OK | 2 | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | 3 | 3 | 4 | bad data | ok | wr | 2 | WR |  |  |  |  | check unit speed. Possible bearing defects at P1H |  |  | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-XTR-3EX-3212 | MS2P-#5 CENTRIFUGE DEFOAMER PUMP | MS2P Curd | 15-3212 | #5 CENTRIFUGE DEFOAMER PUMP |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | bad data | ok | wr | 4 | WR |  |  |  |  | 1x RPM up in motor. Check fasteners, coupling and alignment. |  |  | 2022-01-13
MEM-PRO-015-PCP-PHA-3224 | MS2P-CLARIFIED TANK PUMP | MS2P Curd | 15-3224 | MS2P-CLARIFIED TANK PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | 3 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | bad data | 3 | 4 | 3 | WR |  |  |  |  | The motor vibration data continues to show a dominant shaft speed vibration. Inspect the installation for loose fasteners, base defects, coupling defects and alignment. Look for any other damage in the unit. | 7274538 | #VALUE! | 2022-01-13 |  |  | 6 | 16 | 6
MEM-PRO-015-WSH-CWH-3233 | MS2P-HOLD TANK PUMP TO #1 & #2 WASH CENT | MS2P Curd | 15-3233 | E HOLD PUMP TO 1&2 WASH CENT |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | bad data | ok | ok | ok | WR | [7 empty] | 2022-01-13 |  |  | 6 | 8 | 6
MEM-PRO-015-WSH-CWH-3234 | MS2P-HOLD TANK PUMP TO #3 & #4 WASH CENT | MS2P Curd | 15-3234 | W HOLD PUMP TO 3&4 WASH CENT |  | South | NR | OK | 4 | 4 | WR | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | bad data | ok | ok | ok | WR |  |  |  |  | Possible vane pass peak, continue to monitor |  |  | 2022-01-13 |  |  | 6 | 16 | 6
MEM-PRO-015-WSH-WRE-3237 | MS2P-E WASHING RESLURRY TANK PUMP | MS2P Curd | 15-3237 | E WASHING RESLURRY TANK PUMP | vane pass | South | NR | OK | OK | OK | WR | NR | 2 | NR | 2 | OK | 2 | 3 | OK | 3 | 3 | 2 | 3 | 3 | 3 | 3 | 2 | WR |  |  |  |  | The motor vibration data continues to show dominant shaft speed vibrations, especially in the axial. Inspect the installation for loose fasteners, coupling defects and alignment. Look for any other damage in the unit. | 7248677 | #VALUE! | 2022-01-13 |  |  | 6 | 31 | 6
MEM-PRO-015-WSH-CWH-3246 | MS2P-#1 WASHING CENTRIFUGE | MS2P Curd | 15-3246 | C-30 #1 WASHING CENTRIFUGE |  | South | NR | OK | 4 | 4 | OK | NR | OK | NR | OK | OK | OK | 4 | OK | 2 | 3 | 2 | OK | OK | 1 | 1 | ok | WR |  |  |  |  | flush | Flush |  | 2022-01-13 |  |  |  | 32 | 6
MEM-PRO-015-WSH-CWH-3256 | MS2P-#2 WASHING CENTRIFUGE | MS2P Curd | 15-3256 | C-30 #2 WASHING CENTRIFUGE |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | 4 | 4 | ok | OK | OK | 3 | bad data | 2 | 1 | ok | WR |  |  |  |  | The motor vibration data shows a jump in centrifuge speed vibrations. Inspect the installation for loose fasteners, drive train wear, eccentricity, and alignment. Look for any other damage or defects in the unit. Rated a Class II Defect. | Flush |  | 2022-01-13 |  |  |  | 12 | 6 | [9 empty] | 18" 10 5V1800 PP5811 | 3050 |  | 10 1/2" PP5785 |  | 10ea 18" 5VX1800 PP1338 | 7 to 8 lbf | 6 to 7 lbf | PP5942,PP5946,PP5949 | 4EH
MEM-PRO-015-WSH-CWH-3266 | MS2P-#3 WASHING CENTRIFUGE | MS2P Curd | 15-3266 | C-30 #3 WASHING CENTRIFUGE |  | South | NR | OK | 3 | OK | OK | NR | 3 | NR | OK | OK | OK | 3 | 4 | ok | 3 | 3 | 3 | 3 | 1 | 1 | ok | WR |  |  |  |  | Vibration data on 10-11-21 for the centrifuge has dramatically increased at shaft speed and is dominant in the axial. Clean and flush the unit. Inspect the drive train for wear and alignment. Check all fasteners and structures. Rated a Class IV Defect. | Flush |  | 2022-01-13 |  |  |  | 12 | 6 | [9 empty] | 18" 10 5V1800 PP5811 | 3050 |  | 10 1/2" PP5785 |  | 10ea 18" 5VX1800 PP1338 | 7 to 8 lbf | 6 to 7 lbf | PP5942,PP5946,PP5949 | 3EH
MEM-PRO-015-WSH-CWH-3276 | MS2P-#4 WASHING CENTRIFUGE | MS2P Curd | 15-3276 | C-30 #4 WASHING CENTRIFUGE |  | South | NR | OK | OK | OK | OK | WR | OK | NR | OK | 1 | OK | OK | OK | ok | 4 | 4 | 4 | 4 | 3 | 2 | ok | WR |  |  |  |  | new bowl on 11/16/21 | Flush |  | 2022-01-13 |  |  |  | 12 | 6 | [9 empty] | 18" 10 5V1800 PP5811 | 3050 |  | 10 1/2" PP5785 |  | 10ea 18" 5VX1800 PP1338 | 7 to 8 lbf | 6 to 7 lbf
MEM-PRO-015-WSH-WRE-3289 | MS2P-W WASHING RESLURRY TANK PUMP | MS2P Curd | 15-3289 | W WASHING RESLURRY TANK PUMP |  | South | NR | OK | OK | OK | OK | NR | 3 | NR | OK | OK | OK | 4 | 4 | 1 | 1 | 1 | 1 | 1 | 3 | ok | ok | WR |  |  |  |  | Vibration data for the motor has substantially dropped but still shows a very strong motor 1x RPM vibration. Check all fasteners and structures, the coupling or drive train components for defects, wear, eccentricity, and alignment. Rated a Class II Defect. |  |  | 2022-01-13 |  |  | 6 | 12 | 6 | [9 empty] | 18" 10 5V1800 PP5811 | 3050 |  | 10 1/2" PP5785 |  | 10ea 18" 5VX1800 PP1338 | 7 to 8 lbf | 6 to 7 lbf
MEM-PRO-015-CON-CON-3296 | MS2P-#4 CONCENTRATION CENTRIFUGE | MS2P Curd | 15-3296 | #4 CONCENTRAT CENT SHARPLES |  | South | NR | 3 | OK | 3 | 3 | NR | 3 | NR | OK | 4 | 2 | 2 | 2 | ok | 3 | 3 | 3 | 4 | 4 | 1 | 2 | WR |  |  |  |  | Unit is still showing high acceleration in the C2 bearing above the spectrum F-max. The bearing is in distress. possible cage vibrations are greatly reduces. Continue to monitor closely. Make sure unit bearings are lubricated. | 7253918 | #VALUE! | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-CON-CON-3296 | MS2P-#4 CONCENTRATION CENTRIFUGE | MS2P Curd | 15-3296-08 | #4 CON CENTRIFUGE OIL PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | ok | NR | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-CON-CON-3304 | MS2P-#2 CONCENTRATION CENTRIFUGE | MS2P Curd | 15-3304 | #2 CONCENTRATI CENT SHARPLES |  | South | NR | OK | 2 | 2 | WR | NR | OK | NR | 2 | 2 | 3 | 3 | 2 | 2 | 3 | 2 | 1 | 1 | 2 | 2 | 1 | NR |  |  |  |  | The centrifuge C1 vibration is still excessive at shaft speed. Clean and flush the centrifuge and inspect the installation for any deficiencies. Check the bearings for slight internal looseness, loose fasteners, or for being cocked. | flush |  | 2021-12-13 |  |  |  | 16 | 6
MEM-PRO-015-CON-CON-3304 | MS2P-#2 CONCENTRATION CENTRIFUGE | MS2P Curd | 15-3304-08 | #2 CONCENTRATI CENT OIL PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-CON-CON-3320 | MS2P-#3 CONCENTRATION CENTRIFUGE | MS2P Curd | 15-3320 | #3 CONCENTRATI CENT SHARPLES |  | South | NR | 2 | 3 | OK | OK | NR | 3 | NR | OK | 2 | 1 | 1 | 3 | 1 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | WR |  |  |  |  | Centrifuge still has a large shaft speed vibration in the bearings including a few low harmonics. Clean and flush the unit. Check all fasteners. Rated a Class II Defect. | 7248661 | #VALUE! | 2022-01-13 | 4/18/21 - Bolts broke on pillow block bearing to sharple |  |  | 16 | 6 | [28 empty] | s | 36
MEM-PRO-015-CON-CON-3320 | MS2P-#3 CONCENTRATION CENTRIFUGE | MS2P Curd | 15-3320-08 | #3 CONCENTRATION CENT OIL P |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-IDN-IDF-3350 | MS2P-N CHILL TANK PUMP | MS2P Curd | 15-3350 | MS2P-N CHILL TANK PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | OK | NR | NR | NR | ok | ok | bad data | OK | OK | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-IDN-IDF-3352 | MS2P-S. CHILL TANK PUMP | MS2P Curd | 15-3352 | MS2P-SOUTH CHILL TANK PUMP |  | South | NR | 3 | 3 | NR | 3 | NR | NR | NR | NR | 4 | 3 | OK | 3 | 3 | 3 | NR | 2 | bad data | ok | ok | 1 | WR |  |  |  |  | Motor bearings are gone. Replace ASAP | 7274539 |  | 2022-01-13 | #N/A |  |  | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-CON-CON-4085 | MS2P-#1 CONCENTRATION CENTRIFUGE | MS2P Curd | 15-4085 | #1 CONCENTRATI CENT SHARPLES |  | South | NR | OK | 3 | OK | OK | NR | OK | NR | OK | OK | 3 | 3 | WR | ok | 3 | 3 | 2 | 3 | 3 | 4 | 4 | WR |  |  |  |  | Clean and flush | flush |  | 2022-01-13 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-CON-CON-4085 | MS2P-#1 CONCENTRATION CENTRIFUGE | MS2P Curd | 15-4085-08 | #1 CONCENTRATION CENT OIL P |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-UTL-HRC-4452 | MS2P-WASTE WATER PUM | MS2P Curd | 15-4452 | WASTE WATER PUMP |  | South | NR | 2 | OK | OK | WR | NR | 2 | NR | 2 | OK | 4 | 3 | 3 | 3 | 3 | 3 | 3 | bad data | 4 | wr | 2 | WR |  |  |  |  | 3x pump, process issue | 7267187 | PDM repair | 2022-01-13 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-010-BLD-AHU-8095 | MRAL-VENT EXHAUST FAN | MS2P Dryer Dry | 10-8095-0 | MRAL-BAG H VENT EXHAUST FAN |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | ok | ok | WR |  |  |  |  | worn components. Rated a Class I Defect. |  |  | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-PKG-BLD-3710 | MS2P-BLENDER - RIBBON | MS2P Dryer Dry | 15-3710 | MS2P-BLENDER - RIBBON |  | South | 4 | 4 | 4 | 4 | OK | NR | OK | NR | OK | 3 | 3 | 2 | 2 | OK | OK | OK | OK | OK | OK | wr | 4 | WR |  |  |  |  | Check unit speed. | done |  | 2022-01-13 | Scheduled |  | 12
MEM-PRO-015-PKG-BLD-3712 | MS2P-BLENDER ASP FAN | MS2P Dryer Dry | 15-3712 | MS2P-BLENDER ASP FAN |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 2 | repair | repair | 2 | NR | NR | ok | NR |  |  |  |  | First data on unit. Spectrum shows a few vibration peaks of interest. We suspect drive train issues and possible imbalance. Ensure all fasteners are tight and structures are free of defects. Inspect drive train components for wear and alignment. Please make sure fan motor and speed is correct in the database. Rated a Class III Defect. | 7263433 | #VALUE! | 2021-09-15 |  |  | 1 | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-PKG-PAK-3720 | MS2P-BB ROTARY SCREENER | MS2P Dryer Dry | 15-3720 | #2 AZO BB ROTARY SCREENER |  | South | NR | NR | OK | NR | OK | NR | NR | NR | OK | OK | OK | OK | NR | ok | NR | ok | ok | bad data | ok | ok | ok | WR | [7 empty] | 2022-01-13 |  |  | 1 | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-PKG-PAK-3727 | MS2P-PACKER ROTARY SCREENER | MS2P Dryer Dry | 15-3727 | 1 AZO PACKER ROTARY SCREENER |  | South | NR | OK | NR | NR | OK | NR | NR | NR | OK | 4 | 4 | 4 | 3 | 3 | NR | WR | WR | 3 | ok | wr | 4 | WR |  |  |  |  | Multiple vibration peaks below 100 Hz. need to confirm shaft speed. Inspect fasteners and drive train components. | done |  | 2022-01-13 |  |  | 1 | 16 | 6
MEM-PRO-015-SPR-PRC-3980 | MS2P-ISOLATE PARTICLE SIZING FAN | MS2P Dryer Dry | 15-3980 | ISOLATE PARTICLE SIZING FAN |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | NR | ok | ok | ok | ok | ok | ok | WR |  |  |  |  | reflect accurate motor and fan speeds. Inspect the unit. Check all fasteners and drive train |  |  | 2022-01-13 |  |  | 7 | 27 | 6 |  | drain sample with online filtering and oil coolier | [7 empty] | 18" 10 5V1800 PP5811 | 3050 |  | 10 1/2" PP5785 |  | 10ea 18" 5VX1800 PP1338 | 7 to 8 lbf | 6 to 7 lbf
MEM-PRO-015-SPR-DRY-8001 | MS2P-SPRAY DRYER INLET FAN | MS2P Dryer Dry | 15-8001 | MS2P-SPRAY DRYER INLET FAN |  | South | OK | OK | OK | OK | OK | NR | OK | NR | 3 | OK | OK | OK | OK | ok | OK | OK | OK | bad data | ok | wr | OK | WR |  |  |  |  | Confirm RPM on data |  |  | 2022-01-13 |  |  | 12 | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-015-SPR-DRY-8006 | MS2P-COOLING RING FAN | MS2P Dryer Dry | 15-8006 | MS2P-COOLING RING FAN |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | 1 | ok | ok | OK | 4 | 4 | 4 | 4 | wr | 3 | WR |  |  |  |  | F2A 63.75 Hz vibration. Please confirm shaft speed. Multiple harmonic vibrations in fan f2v. check fasteners and bearings for looseness. | 7274540 |  | 2022-01-13 | missed call March IB fan bearing failed |  | 12 | 16 | 6
MEM-PRO-015-SPR-DRY-8008 | MS2P-STATIC FLUID BED FAN | MS2P Dryer Dry | 15-8008 | MS2P-STATIC FLUID BED FAN |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | OK | 4 | 4 | 4 | 4 | 3 | 4 | 3 | ok | ok | ok | ok | WR |  |  |  |  | Rated a Class I Defect. |  |  | 2022-01-13 |  |  | 12 | 8 | 6
MEM-PRO-015-SPR-PRC-8014 | MS2P-PC TRANSFER BLOWER TO ISO SURGE BIN | MS2P Dryer Dry | 15-8014 | PC TRANS BLOWER TO ISO S BIN |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | OK | 4 | 4 | OK | 4 | OK | OK | OK | OK | ok | ok | ok | WR |  |  |  |  | components. Rated a Class II Defect. | done |  | 2022-01-13 |  |  | 6 | 8 | 6
MEM-PRO-015-SPR-DRY-8054 | MS2P-NW BAGHOUSE BLOWER | MS2P Dryer Dry | 15-8054 | #2 CMC NW BAGHOUSE BLOWER |  | South | OK | OK | OK | OK | OK | NR | OK | NR | 3 | 3 | OK | 4 | 4 | 4 | OK | OK | OK | OK | ok | ok | OK | WR |  |  |  |  | Blower bearings show multiple harmonics of input shaft speed. The unit could be under high load and/or starting to show signs of wear. Rated a Class I Defect. |  |  | 2022-01-13 |  |  | 8 | 16 | 6
MEM-PRO-015-SPR-DRY-8064 | MS2P-NE BAGHOUSE BLOWER | MS2P Dryer Dry | 15-8064 | #1 CMC NE BAGHOUSE BLOWER |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | 3 | OK | 4 | 4 | 4 | 4 | ok | ok | ok | ok | ok | ok | WR |  |  |  |  | Harmonics of blower shaft speed have increased recently. We suspect early wear or higher loading. |  |  | 2022-01-13 |  |  | 8 | 16 | 6
MEM-PRO-015-SPR-DRY-8068 | MS2P-SPRAY DRYER N EXHAUST FAN | MS2P Dryer Dry | 15-8068 | #1 SPRAY DRYER N EXHAUST FAN |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | 4 | 4 | 3 | 3 | 3 | OK | OK | OK | OK | ok | ok | OK | WR |  |  |  |  | Confirm speed | done |  | 2022-01-13 |  |  | 12 | 16 | 6
MEM-PRO-015-SPR-DRY-8069 | MS2P-NW & NE BAGHOUSE CONE HEATER | MS2P Dryer Dry | 15-8069 | NW & NE BH CONE HEATER FAN |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | NR | 3 | 3 | 3 | 2 | 2 | 2 | bad data | 3 | 3 | 3 | WR |  |  |  |  | Motor still has a strong fan speed vibration. Inspect the unit drive train components for wear | 7268995 | #VALUE! | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-SPR-DRY-8074 | MS2P-SE BAGHOUSE BLOWER | MS2P Dryer Dry | 15-8074 | #4 CMC SE BAGHOUSE BLOWER |  | South | OK | OK | OK | OK | OK | NR | OK | NR | 3 | 3 | 3 | 4 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | wr | 4 | WR |  |  |  |  | harmonics, slight wear | done |  | 2022-01-13 |  |  | 8 | 16 | 6
MEM-PRO-015-SPR-DRY-8084 | MS2P-SW BAGHOUSE BLOWER | MS2P Dryer Dry | 15-8084 | #3 CMC SW BAGHOUSE BLOWER |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | 4 | 4 | 4 | OK | OK | OK | OK | OK | ok | OK | WR |  |  |  |  | Defect. |  |  | 2022-01-13 |  |  | 8 | 16 | 6
MEM-PRO-015-SPR-DRY-8088 | MS2P-SPRAY DRYER S EXHAUST FAN | MS2P Dryer Dry | 15-8088 | #2 SPRAY DRYER S EXHAUST FAN | jewel | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | 4 | OK | OK | OK | 4 | OK | 4 | 4 | 4 | 4 | ok | ok | WR |  |  |  |  | Possible early defects in the inboard fan bearing. No action required. Rated a Class I Defect. |  |  | 2022-01-13 |  |  | 12 | 16 | 2
MEM-PRO-015-SPR-DRY-8089 | MS2P-SW & SE BAGHOUSE CONE HEATER | MS2P Dryer Dry | 15-8089 | SW & SE BH CONE HEATER FAN |  | South | NR | OK | OK | OK | OK | NR | NR | NR | OK | OK | 4 | 3 | 3 | ok | 3 | 3 | 3 | 4 | 2 | 2 | 3 | WR |  |  |  |  | Motor still has a strong fan speed vibration. Inspect the unit drive train components for wear |  | #VALUE! | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-SPR-DRY-8100 | MS2P-VF BAGHOUSE EXHAUST FAN | MS2P Dryer Dry | 15-8100 | MS2P VF BAGHOUSE EXHAUST FAN |  | South | OK | OK | OK | OK | OK | NR | OK | NR | OK | OK | 3 | 4 | OK | 3 | 3 | 4 | 3 | 3 | 3 | 3 | ok | WR |  |  |  |  | Unit still has a dominant vibration near 25 Hz in the motor and fan. Please adjust the data base to | 7248681 | #VALUE! | 2022-01-13 |  |  | 10 | 16 | 6
MEM-PRO-015-IDN-IDF-3364 | MS2P-IDN FEED PUMP | MS2P Dryer Wet | 15-3364 | MS2P-WEST IDN TANK FEED PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | ok | ok | WR |  |  |  |  | stuck on it also. Rated a Class II Defect. |  |  | 2022-01-13 |  |  | 1 | 16 | 6
MEM-PRO-015-IDN-IDF-3425 | MS2P-E IDN TANK DISCHARGE PUMP | MS2P Dryer Wet | 15-3425 | 2P E IDN TANK DISCHARGE PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | OK | OK | ok | OK | ok | ok | 3 | ok | WR | 4 | WR |  |  |  |  | Increase in acceleration in motor DE bearing |  |  | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-IDN-IDF-3432 | MS2P-EAST IDN PH PUMP | MS2P Dryer Wet | 15-3432 | EAST IDN TANK CIRC PH PUMP |  | South | NR | OK | OK | OK | OK | NR | 3 | NR | 3 | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | ok | ok | WR | [7 empty] | 2022-01-13 |  |  |  | 16 | 6
MEM-PRO-015-BGY-FCS-3461 | MS2P-E VACUUMIZER CONDENSATE PUMP | MS2P Dryer Wet | 15-3461 | E VACUUMIZER CONDENSATE PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | OK | OK | ok | OK | OK | OK | ok | ok | ok | ok | WR | [7 empty] | 2022-01-13 |  |  | 4 | 16 | 6
MEM-PRO-015-BGY-FCS-3471 | MS2P-E VACUUMIZER VACUUM PUMP | MS2P Dryer Wet | 15-3471 | E VACUUMIZER VACUUM PUMP | MCA | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | OK | OK | ok | OK | OK | OK | 2 | ok | ok | ok | WR |  |  |  |  | Motor data shows a large increase in vibration at very near 360 Hz. This is odd for an AC motor unless it is on a frequency drive. Inspect the unit for electrical issues. Rated a Class III Defect. | done |  | 2022-01-13 |  |  | 6 | 16 | 6
MEM-PRO-015-BGY-FCS-3475 | MS2P-E VACUUMIZER DISCHARGE PUMP | MS2P Dryer Wet | 15-3475 | E VACUUMIZER DISCHARGE PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | ok | ok | WR |  |  |  |  | vane pass sometimes | vane pass |  | 2022-01-13 | process issues |  | 4 | 16 | 6
MEM-PRO-015-BGY-FCS-3534 | MS2P-W VACUUMIZER CONDENSATE PUMP | MS2P Dryer Wet | 15-3534 | W VACUUMIZER CONDENSATE PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | ok | ok | WR | [7 empty] | 2022-01-13 |  |  | 4
MEM-PRO-015-BGY-FCS-3539 | MS2P-W VACUUMIZER VACUUM PUMP | MS2P Dryer Wet | 15-3539 | W VACUUMIZER VACUUM PUMP |  | South | NR | OK | OK | OK | OK | NR | 2 | NR | 2 | 2 | 2 | 3 | 3 | 3 | OK | 4 | 4 | 4 | 4 | 4 | 4 | WR |  |  |  |  | Pump has dominant 3x RPM vibration and multiple shaft speed harmonics. Slight wear. |  |  | 2022-01-13 |  |  | 6 | 16 | 2 | [24 empty] | 12:05AM
MEM-PRO-015-IDN-HYS-3562 | MS2P-E HYDROLYSIS DISCHARGE PUMP | MS2P Dryer Wet | 15-3562 | E HYDROLISIS DISHARGE PUMP |  | South | NR | NR | OK | OK | OK | NR | NR | NR | NR | 3 | OK | OK | OK | 2 | 3 | 3 | 3 | 3 | 3 | bad data | 4 | WR |  |  |  |  | 1x RPM pump vibration. Watch only | 7257555 | #VALUE! | 2022-01-04 |  |  |  | 24 | 6
MEM-PRO-015-IDN-HYS-3572 | MS2P-W HYDROLYSIS DISCHARGE PUMP | MS2P Dryer Wet | 15-3572 | W HYDROLISIS DISCHARGE PUMP |  | South | NR | OK | OK | NR | OK | NR | OK | NR | NR | NR | OK | OK | NR | ok | OK | OK | OK | NR | ok | ok | ok | NR | [7 empty] | 2021-12-02 |  |  |  | 16 | 6
MEM-PRO-015-BGY-FCS-9241 | MS2P-W VACUUMIZER DISCHARGE PUMP | MS2P Dryer Wet | 15-9241 | W VACUUMIZER DISCHARGE PUMP | rpm | South | NR | OK | 3 | 3 | OK | NR | 3 | NR | 3 | 3 | 2 | OK | OK | ok | 2 | 3 | 3 | 3 | 4 | WR | 4 | WR |  |  |  |  | Confirm shaft speeds | done |  | 2022-01-13 |  |  | 4 | 16 | 6
MEM-PRO-010-STS-TK2-3827 | MS2P-FEED TRANSFER BLOWER | MS2P Feed Dryer | 10-3827-0 | FEED TRANSFE LOAD OUT BLOWER |  | South | NR | NR | OK | NR | OK | NR | NR | NR | NR | OK | ok | OK | OK | NR | OK | 4 | 4 | wr | WR | wr | NR | NR |  |  |  |  | Half harmonics are present in the data if the speed is correct. Half harmonics indicate looseness. |  |  | 2021-11-22 |  |  |  | 16 | 6
MEM-PRO-015-FED-SLT-3800 | MS2P-FEED PADDLE MIXER | MS2P Feed Dryer | 15-3800 | MS2P-FEED PADDLE MIXER |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | OK | OK | OK | OK | wr | NR | NR |  |  |  |  | Rated a Class I Defect. |  |  | 2021-11-22 |  |  | 16 | 16 | 6
MEM-PRO-015-FED-SLT-3801 | MS2P-INFEED SCREW CONVEYOR | MS2P Feed Dryer | 15-3801 | MS2P-INFEED SCREW CONVEYOR |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | 4 | wr | WR | wr | NR | NR |  |  |  |  | First data taken. Possible distress in bearing B1. Please confirm shaft speed. Rated a Class I Defect. |  |  | 2021-11-22 |  |  | 6 | 16 | 2
MEM-PRO-015-FED-FED-3803 | MS2P-FEED DRYER | MS2P Feed Dryer | 15-3803 | 2P FEED DRYER-(DRUM DRIVE) |  | South | NR | NR | OK | NR | OK | NR | NR | NR | NR | OK | ok | OK | OK | NR | OK | OK | OK | OK | OK | wr | NR | NR | [7 empty] | 2021-11-22 |  |  | 24 | 16 | 6 | [6 empty] | Yes
MEM-PRO-015-FED-FED-3828 | MS2P-FEED RECYCLE BLOWER | MS2P Feed Dryer | 15-3828 | MS2P-FEED RECYCLE BLOWER |  | South | NR | NR | OK | NR | OK | NR | NR | NR | NR | OK | ok | 3 | ok | NR | OK | 4 | 4 | wr | WR | wr | NR | NR |  |  |  |  | Shaft speed and harmonic vibration peaks are up. Check fastener, structure, and belts and sheaves for wear, alignment, and eccentricity. Rated a Class I Defect. |  |  | 2021-11-22 |  |  | 6 | 24 | 6
MEM-PRO-015-FED-FED-3842 | MS2P-FEED DRYER FEED TRANSFER BLOWER | MS2P Feed Dryer | 15-3842 | FEED DRYER TRANSFER BLOWER |  | South | NR | NR | OK | NR | OK | NR | NR | NR | NR | OK | ok | OK | OK | NR | OK | 4 | 4 | wr | WR | wr | NR | NR |  |  |  |  | Motor has 1x and 2x fan speed vibrations. Check fastener, structure, and belts and sheaves for wear, alignment, and eccentricity. Rated a Class I Defect. |  |  | 2021-11-22 |  |  | 6 | 24 | 6
MEM-PRO-015-FED-FED-3843 | MS2P-FEED DRYER FILTER TRANSFER BLOWER | MS2P Feed Dryer | 15-3843 | 2P FD FILTER TRANSFER BLOWER |  | South | NR | NR | OK | NR | OK | NR | NR | NR | NR | OK | ok | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | NR | NR |  |  |  |  | Blower shaft speed vibrations are still strong in the motor verticals. Check drive train components for wear, eccentricity, alignment, and ensure all structures and fasteners are good. The motor data still shows that possible early bearing defect frequencies are present. Ensure the motor bearings are lubricated if applicable. Rated a Class II Defect. | 7235955 | #VALUE! | 2021-11-22 |  |  | 6 | 16 | 6
MEM-PRO-015-FED-FED-3844 | MS2P-FEED DRYER EXHAUST FAN | MS2P Feed Dryer | 15-3844 | MS2P-FEED DRYER EXHAUST FAN |  | South | NR | NR | OK | NR | OK | NR | NR | NR | 3 | 3 | 3 | 2 | 4 | 4 | 4 | 3 | 2 | 3 | 3 | 2 | NR | NR |  |  |  |  | fasteners are tight. Rated a Class IV Defect. | 7257556 | #VALUE! | 2021-11-22 |  |  | 6 | 16 | 6
MEM-PRO-015-FED-FED-3847 | MS2P-FEED DRYER INLET FAN | MS2P Feed Dryer | 15-3847 | MS2P-FEED DRYER INLET FAN |  | South | NR | NR | OK | NR | 3 | NR | NR | NR | NR | OK | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | ok | NR | NR |  |  |  |  | loose bearings |  |  | 2021-11-22 |  |  | 6 | [26 empty] | 12:34AM
MEM-PRO-015-FED-FED-3848 | MS2P-FEED DRYER COMBUSTION FAN | MS2P Feed Dryer | 15-3848 | FEED DRYER COMBUSTION FAN |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 2 | 1 | 1 | NR | NR | 3 | NR | NR |  |  |  |  | still belts and balance | 7271850 | #VALUE! | 2021-11-22 |  |  | 6
MEM-PRO-015-FED-FED-3862 | MS2P-FEED MILL RCVR VENT FAN | MS2P Feed Dryer | 15-3862 | MS2P-FEED MILL RCVR VENT FAN |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 3 | 2 | 2 | 2 | 2 | 2 | NR | NR |  |  |  |  | the pump and looseness in the bearings or fits. Inspect as time allows. Rated a Class I Defect. | 7257614 | #VALUE! | 2021-11-22 |  |  | 6 | 16 | 6
MEM-PRO-015-FED-FED-3863 | MS2P-FEED RECYCLE RECEIVER VENT FAN | MS2P Feed Dryer | 15-3863 | FEED RECYC RECEIVER VENT FAN |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 3 | 3 | NR | NR | 3 | 3 | NR | NR |  |  |  |  | First data. Vibration data for the inboard fan bearing shows a strong non-synchronous vibration with multiple harmonics. This analysis is based on the fan speed being correct in the database. We suspect outer race bearing defects. Rated a Class II Defect. | 7257615 | #VALUE! | 2021-11-22 |  |  | 6 | 16 | 6 | [24 empty] | 12:25AM
MEM-PRO-015-CIP-SAC-4019 | MS2P-CIP CAUSTIC RECIRC HEAT PUMP | MS2P Feed Dryer | 15-4019 | CIP CAUSTIC RECIRC HEAT PUMP |  | South | NR | NR | NR | OK | OK | NR | 3 | NR | NR | 2 | 3 | 3 | 3 | 2 | 3 | 3 | 3 | 3 | 1 | 2 | 2 | NR |  |  |  |  | Pump vibrations are always near 1"/second. Unit needs evaluation. | 7267853 | #VALUE! | 2021-12-23 |  |  | 8 | 16 | 2 | [24 empty] | 12:18AM
MEM-PRO-015-CIP-CAC-4027 | MS2P-CIP FEED PUMP TO CURD FRONT END | MS2P Feed Dryer | 15-4027 | #4 CIP FEED PUMP 2 FRONT END |  | South | NR | NR | NR | NR | NR | NR | OK | NR | NR | OK | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | ok | NR |  |  |  |  | Data taken on machine not running |  |  | 2021-12-23 |  |  | 8 | [26 empty] | 12:08AM
MEM-PRO-015-CIP-CAC-4028 | MS2P-CIP FEED PUMP TO CURD BACK END | MS2P Feed Dryer | 15-4028 | #2 CIP FEED PUMP 2 BACK END |  | South | NR | NR | NR | NR | NR | NR | OK | NR | NR | OK | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | ok | NR |  |  |  |  | Data taken on machine not running |  |  | 2021-12-23 |  |  | 8 | 16 | 3
MEM-PRO-015-CIP-DAC-4050 | MS2P-CIP FEED PUMP TO SWITCH STATION | MS2P Feed Dryer | 15-4050 | #1 CIP FEED PUMP-SWITCH STAT |  | South | NR | NR | NR | NR | NR | NR | 3 | NR | 3 | 3 | NR | NR | NR | ok | NR | NR | NR | NR | NR | NR | ok | NR |  |  |  |  | Data taken on machine not running |  |  | 2021-12-23 |  |  | 8 | 16 | 3
MEM-PRO-015-CIP-DAC-4051 | MS2P-CIP FEED PUMP TO SWITCH STATION | MS2P Feed Dryer | 15-4051 | #3 CIP FEED PUMP-SWITCH STAT |  | South | NR | NR | NR | NR | NR | NR | OK | NR | NR | OK | NR | NR | NR | ok | NR | NR | NR | ok | NR | NR | ok | NR |  |  |  |  | Data taken on machine not running |  |  | 2021-12-23 |  |  | 8 | 16 | 3
MEM-PRO-015-FED-BLP-4107 | MS2P-BELT PRESS WASH WATER CIRC PUMP | MS2P Feed Dryer | 15-4107 | BELT PRES WASH WTR CIRC PUMP |  | New South | [29 empty] | 2021-07-29 |  |  | 4 | 16 | 3 | bar: NR to NR
MEM-PRO-015-FED-BLP-4108 | MS2P-BELT PRESS DISCHARGE SCREW CONV #5 | MS2P Feed Dryer | 15-4108 | BELT PRES DISCH SCREW CONV 5 |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 4 | 2 | 2 | 2 | 2 | NR | NR |  |  |  |  | Limited data showing a possible 2x RPM motor axial vibration, a large, elevated noise floor in the B1H measurement, and note codes showing “FIELD ALERT” leads us to report this as a Rated a Class III Defect. Please inspect this installation completely at the next opportunity. | 7271853 | #VALUE! | 2021-11-22
MEM-PRO-015-FED-BLP-4110 | MS2P-BELT PRESS PRESSURE PUMP | MS2P Feed Dryer | 15-4110 | BELT PRESS PRESSURE PUMP |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | ok | NR | WR | NR | NR | NR | [7 empty] | 2021-10-04 |  |  | 4
MEM-PRO-015-UTL-PRW-4203 | MS2P-HOT WTR PUMP PRESS IND IN | MS2P Feed Dryer | 15-4203 | HOT WTR PUMP PRESS IND IN |  | South | NR | NR | NR | 3 | 3 | NR | 4 | NR | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | NR |  |  |  |  | High1x RPM axial vibration in motor. Check fasteners, coupling and alignment. | 7259892 | #VALUE! | 2021-12-23 | [29 empty] | 4:16AM
MEM-PRO-015-UTL-PRW-4209 | MS2P-90 DEG F PROCESS WTR PUMP #2 | MS2P Feed Dryer | 15-4209 | 90 DEG F PROCESS WTR PUMP #2 |  | South | NR | NR | NR | OK |  | NR | OK | NR | 3 | OK | NR | 3 | 4 | NR | NR | NR | 3 | NR | NR | 4 | 4 | NR |  |  |  |  | 1x RPM pump vibration. Watch only |  |  | 2021-12-23 |  |  |  | 16 | 5 | [24 empty] | 4:22
MEM-PRO-014-CON-CRE-2184 | MSP-WET GRINDER FEED PUMP | MSP Curd | 14-2184 | MSP-WET GRINDER FEED PUMP |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | OK | OK | OK | OK | OK | ok | NR |  |  |  |  | fasteners, misalignment bent shaft/eccentricity or a coupling issue. Rated a Class I Defect. |  |  | 2021-12-21 |  |  | 4 | 16 | 2 | [24 empty] | 4:28AM
MEM-PRO-014-WEI-WIS-3039 | MSP-FLAKE BIN ASPIRATION FAN #3 | MSP Curd | 14-3039 | FLAKE BIN N ASPIRATION FAN 3 |  | South | NR | OK | OK | NR | OK | NR | NR | NR | NR | NR | OK | 4 | OK | NR | OK | 4 | 4 | 4 | ok | wr | 4 | NR |  |  |  |  | Check fasteners and belts |  |  | 2021-12-21
MEM-PRO-014-WEI-WIS-3050 | MSP-FLAKE BIN EXHAUST FAN | MSP Curd | 14-3050 | S FLAKE BIN EXHAUST ASP FAN |  | South | NR | OK | OK | OK | OK | NR | NR | NR | NR | 4 | OK | OK | 3 | OK | OK | OK | OK | OK | OK | OK | 4 | NR |  |  |  |  | check fasteners, belt alignment, and tension. | done |  | 2021-12-16 |  |  | 4 | 8 | 2 | [6 empty] | Yes
MEM-PRO-014-WEI-WIS-3085 | MSP-WET IN CROSS SCREW CONVEYOR | MSP Curd | 14-3085 | WET IN CROSS SCREW CONVEYOR |  | South | NR | OK | OK | OK | OK | NR | NR | NR | NR | OK | OK | OK | OK | 4 | OK | OK | OK | OK | OK | OK | ok | NR |  |  |  |  | Motor vibrations have increased, and the data is dominated by a 10 Hz vibration. Inspect the unit and structure for issues. Rated a Class I Defect. |  |  | 2021-12-16 |  |  | 4 | 16 | 2
MEM-PRO-014-WEI-WIS-3087 | MSP-FLAKE GRAVIMETRIC FEEDER | MSP Curd | 14-3087 | FLAKE ACRISON FEEDER |  | South | NR | OK | OK | OK | OK | NR | NR | NR | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | NR | [7 empty] | 2021-12-16 |  |  | 4 | 16 | 2
MEM-PRO-014-WEI-WIS-3090 | MSP-WET IN XFER PUMP | MSP Curd | 14-3090 | MSP WET IN XFER PUMP |  | South | NR | OK | OK | OK | OK | NR | NR | NR | NR | 4 | OK | OK | 3 | 4 | 3 | 3 | 1 | 4 | ok | ok | ok | NR |  |  |  |  | and alignment. Clean and Flush. Rated a Class II Defect. |  |  | 2021-12-16 |  |  | 4
MEM-PRO-014-WEI-WIS-3108 | MSP SULFITE WORK TANK DISCHARGE PUMP | MSP Curd | 14-3108 | SULFITE WORK TANK DISCH PUMP |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | NR | ok | ok | 4 | wr | ok | NR |  |  |  |  | Motor axial is up at shaft speed. Check the coupling and alignment as time allows. Rated a Class I |  |  | 2021-12-21 |  |  | 4 | 16 | 7
MEM-PRO-014-XTR-1EX-3114 | MSP-1ST EXTRACTION FEED PUMP | MSP Curd | 14-3114 | MSP-1ST EXTRACTION FEED PUMP |  | South | NR | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | NR | OK | OK | ok | NR | [7 empty] | 2021-12-21 |  |  | 6 | 28 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-2EX-3130 | MSP-2ND EXT FEED PUMP | MSP Curd | 14-3130 | MSP-2ND EXT FEED PUMP |  | South | NR | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | NR | [7 empty] | 2021-12-21 |  |  | 6 | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-1EX-3133 | MSP-#1 1ST EXT CENT DEFOAMER PUMP | MSP Curd | 14-3133 | #1-1ST EXT CENT DEFOAM PUMP |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | 4 | OK | OK | ok | OK | OK | OK | OK | OK | OK | 4 | NR |  |  |  |  | possible electrical issue. Check connections |  |  | 2021-12-21 |  |  | 6 | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-1EX-3137 | MSP-#2 1ST EXT CENT DEFOAMER PUMP | MSP Curd | 14-3137 | #2 1ST EXT CENT DEFOAM PUMP |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | 4 | 4 | 3 | 2 | 3 | OK | 3 | ok | ok | ok | ok | ok | NR |  |  |  |  | Motor data still indicates some misalignment due to a possible dominant 2x motor RPM vibration at near 0.6”/sec velocity peak. Check unit for coupling alignment issues. Rated a Class II Defect. | done |  | 2021-12-21 |  |  | 6 | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-1EX-3141 | MSP-#1 1ST EXTRACTION CENTRIFUGE | MSP Curd | 14-3141 | #1 1ST EXTRACTION CENTRIFUGE |  | South | OK | OK | 4 | 4 | 4 | OK | OK | OK | NR | 2 | 1 | 1 | 4 | 1 | 2 | 3 | 1 | 2 | 2 | 3 | 3 | NR |  |  |  |  | Jump in M4H bearing defect frequencies, and still elevated M2H bearing defects frequencies. Both motors have defects. | 7269878 | #VALUE! | 2021-12-16 |  |  |  | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-1EX-3141 | MSP-#1 1ST EXTRACTION CENTRIFUGE | MSP Curd | 14-3141-08 | #1 1ST EXT CENTRIFUGE OIL P |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | NR |  |  |  |  | peak overall. Clean, flush and inspect. Rated a Class III Defect. |  |  | 2021-12-21 |  |  |  | 16 | 7
MEM-PRO-014-XTR-3EX-3149 | MSP-#4 3RD EXTRACTION CENTRIFUGE | MSP Curd | 14-3149 | #4 3RD EXT CENTRIFUGE SHARPL |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | 4 | NR | 2 | 3 | 3 | 3 | 2 | 2 | 2 | 3 | 4 | NR |  |  |  |  | Clean and flush | flush |  | 2021-12-16 |  |  |  | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-3EX-3149 | MSP-#4 3RD EXTRACTION CENTRIFUGE | MSP Curd | 14-3149-08 | #4 3RD EXT CENTRIFUGE OIL P |  | South | OK | OK | OK | OK | OK | NR | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | 3 | NR |  |  |  |  | Possible motor lubrication or bearing defect due to increase in acceleration M1H | 7277496 |  | 2021-12-21 |  |  |  | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-1EX-3151 | MSP-#2 1ST EXTRACTION CENTRIFUGE | MSP Curd | 14-3151 | #2 1ST EXT CENTRIFUGE SHARPL |  | South | OK | OK | OK | OK | OK | NR | 2 | OK | NR | OK | 4 | 2 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 3 | 4 | NR |  |  |  |  | Clean and flush | flush |  | 2021-12-16 |  |  |  | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-1EX-3151 | MSP-#2 1ST EXTRACTION CENTRIFUGE | MSP Curd | 14-3151-08 | #2 1ST EXT CENTRIFUGE OIL P |  | South | OK | OK | NR | OK | OK | OK | OK | OK | NR | 3 | 3 | OK | 3 | ok | OK | OK | OK | OK | OK | OK | ok | NR |  |  |  |  | issues. Rated a Class IV Defect. | done |  | 2021-12-21 |  |  |  | 32 | 6
MEM-PRO-014-XTR-1EX-3161 | MSP-#3 1ST EXTRACTION CENTRIFUGE | MSP Curd | 14-3161 | #3 1ST EXT CENTRIFUGE SHARPL |  | South | OK | OK | 4 | 4 | 4 | OK | OK | OK | NR | OK | 3 | 1 | 2 | 2 | 3 | 2 | 1 | 2 | 2 | 3 | 4 | NR |  |  |  |  | Clean and flush |  |  | 2021-12-16 |  |  |  | 32 | 6
MEM-PRO-014-XTR-1EX-3161 | MSP-#3 1ST EXTRACTION CENTRIFUGE | MSP Curd | 14-3161-08 | #3 1ST EXT CENTRIFUGE OIL P |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | NR | ok | ok | NR | [7 empty] | 2021-12-21 |  |  |  | 27 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-2EX-3171 | MSP-#5 CENTRIFUGE 2ND EXTRACTION | MSP Curd | 14-3171 | #5 CETRIFUGE 2ND EXT SHARPL | rpm | South | OK | OK | 4 | 4 | 4 | OK | OK | OK | NR | OK | OK | 3 | 3 | 2 | 2 | 3 | 2 | 2 | 3 | 3 | 2 | NR |  |  |  |  | Clean and flush, and check main drive belt tension and sheave alignment. |  |  | 2021-12-16 |  |  | 1 | 12 | 6
MEM-PRO-014-XTR-2EX-3171 | MSP-#5 CENTRIFUGE 2ND EXTRACTION | MSP Curd | 14-3171-08 | #5 CENTRIFUGE 2ND EXT OIL P |  | South | OK | OK | NR | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | ok | ok | ok | NR | [7 empty] | 2021-12-21 |  |  | 1 | 12 | 6
MEM-PRO-014-XTR-2EX-3179 | MSP-#4 CENTRIFUGE 2ND EXT DEFOAMER PUMP | MSP Curd | 14-3179 | #4 CENT 2ND EXT DEFOAM PUMP |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | 4 | OK | NR | ok | OK | 4 | 3 | bad data | 3 | ok | 4 | NR |  |  |  |  | 1x RPM vibration. Chec base, fasteners, coupling and alignment. |  |  | 2021-12-21 |  |  |  | 12 | 6
MEM-PRO-014-XTR-1EX-3207 | MSP-1ST EXT DEF PUMP (#3 CENTRIFUGE) | MSP Curd | 14-3207 | #3 1ST EXT DEF CENT PUMP |  | South | OK | OK | NR | OK | OK | OK | OK | OK | NR | OK | OK | OK | 4 | NR | 2 | OK | 4 | bad data | NR | ok | ok | NR | [7 empty] | 2021-12-21 |  |  | 6 | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-XTR-2EX-3212 | MSP-#5 CENTRIFUGE 2ND EXT DEFOAMER PUMP | MSP Curd | 14-3212 | #5 CENT 2ND EXT DEFOAM PUMP |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | ok | 4 | NR |  |  |  |  | cavitation? |  |  | 2021-12-21 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-PCP-PHA-3224 | MSP-CLARIFIED TANK PUMP | MSP Curd | 14-3224 | MSP-CLARIFIED TANK PUMP |  | South | NR | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | ok | ok | NR |  |  |  |  | Class I Defect. |  |  | 2021-12-21 |  |  | 4 | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-WSH-WRE-3233 | MSP-PREC TANK #1 PUMP | MSP Curd | 14-3233 | PREC HOLD TANK #1 SOUTH PUMP |  | South | NR | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | NR | OK | ok | ok | NR | [7 empty] | 2021-12-21 |  |  | 4 | 16 | 6
MEM-PRO-014-WSH-WRE-3234 | MSP-PREC TANK #2 PUMP | MSP Curd | 14-3234 | PREC HOLD TANK #2 NORTH PUMP |  | South | NR | OK | 4 | 4 | OK | NR | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | NR | OK | ok | ok | NR |  |  |  |  | vane pass, possible restriction |  |  | 2021-12-21 |  |  | 4
MEM-PRO-014-CON-WRE-3237 | MSP-E. WASHING RESLURRY TANK PUMP | MSP Curd | 14-3237 | E WASHING RESLURRY TANK PUMP |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | 3 | 4 | 4 | 4 | 3 | OK | OK | OK | ok | ok | 4 | NR |  |  |  |  | Possiible looseness in P1/P2 bearing measurements |  |  | 2021-12-16 |  |  | 4 | 16 | 6 | [24 empty] | TAR WO
MEM-PRO-014-WSH-CWH-3246 | MSP-#1 WASHING CENTRIFUGE | MSP Curd | 14-3246 | C30 #1 WASHING CENTRIFUGE |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | 3 | 4 | OK | OK | 3 | ok | 2 | 3 | 2 | NR |  |  |  |  | Motor 1x RPM us up in multiple points. Inspect structure, fasteners, and drive train for wear and alignment. | 7277497 |  | 2021-12-21 |  |  |  | 32 | 7
MEM-PRO-014-WSH-CWH-3256 | MSP-#2 WASHING CENTRIFUGE | MSP Curd | 14-3256 | C30 #2 WASHING CENTRIFUGE |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | 4 | OK | 3 | 2 | 3 | OK | OK | 2 | 3 | 2 | ok | ok | NR |  |  |  |  | train for wear, run out and alignment. Check all fasteners and structures. Rated a Class II Defect. |  |  | 2021-12-21 |  |  |  | 16 | 7
MEM-PRO-014-WSH-CWH-3266 | MSP-#3 WASHING CENTRIFUGE | MSP Curd | 14-3266 | C30 #3 WASHING CENTRIFUGE |  | South | OK | OK | 3 | 3 | 3 | OK | OK | OK | NR | OK | OK | OK | 2 | NR | OK | OK | 3 | 3 | 3 | ok | ok | NR |  |  |  |  | Elevated centrifuge speed vibration in centrifuge axial. Motor speed vibrations are also evident. Inspect |  |  | 2021-12-21 |  |  |  | 32 | 7
MEM-PRO-014-WSH-CWH-3276 | MSP-#4 WASHING CENTRIFUGE | MSP Curd | 14-3276 | C30 #4 WASHING CENTRIFUGE |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | 4 | OK | 4 | 4 | 4 | 4 | OK | 3 | 3 | 3 | 4 | ok | NR | [7 empty] | 2021-12-21 |  |  |  | 16 | 6
MEM-PRO-014-WSH-WRE-3289 | MSP-W. WASHING RESLURRY PUMP | MSP Curd | 14-3289 | WEST WASHING RESLURRY PUMP |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | 4 | OK | OK | 3 | 3 | 3 | OK | 4 | bad data | ok | 3 | 2 | NR |  |  |  |  | Strong shaft speed and a few harmonics vibrations in the pump. 1x anx 3x RPM vibrations are dominant. Check all fasteners, the coupling, shaft alignment, and impeller if unit has 3 vanes. | 7269879 | #VALUE! | 2021-12-16 |  |  | 4 | 16 | 6 | [6 empty] | Yes
MEM-PRO-014-CON-CON-3296 | MSP-#8 CONCENTRATION CENTRIFUGE | MSP Curd | 14-3296 | #8 CON CNETRIFUGE SHARPLE |  | South | OK | OK | 4 | 4 | 4 | OK | OK | OK | NR | OK | 4 | 3 | 3 | 3 | 2 | 1 | 1 | 3 | 4 | 4 | 4 | NR |  |  |  |  | Clean and flush | flush |  | 2021-12-16 | Bolwl changed 4/7/21 |  |  | 16 | 6
MEM-PRO-014-CON-CON-3296 | MSP-#8 CONCENTRATION CENTRIFUGE | MSP Curd | 14-3296-08 | #8 CON CENTRIFUGE OIL PUMP |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | NR |  |  |  |  | the drive train for wear, run out and alignment. Clean and flush the centrifuge. Check all fasteners and |  |  | 2021-12-21 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-CON-CON-3304 | MSP-#6 CONCENTRATION CENTRIFUGE | MSP Curd | 14-3304 | #6 CON CENTRIFUGE SHARPLE |  | South | OK | OK | NR | OK | OK | NR | OK | NR | NR | OK | 3 | NR | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 4 | NR |  |  |  |  | Clean and flush | flush |  | 2021-12-16 |  |  | 1 | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-CON-CON-3304 | MSP-#6 CONCENTRATION CENTRIFUGE | MSP Curd | 14-3304-08 | #6 CON CENTRIFUGE OIL PUMP |  | South | OK | OK | NR | OK | OK | OK | OK | NR | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | NR |  |  |  |  | structures. Rated a Class II Defect. |  |  | 2021-12-21 |  |  | 1 | 16 | 6
MEM-PRO-014-CON-CON-3320 | MSP-#7 CONCENTRATION CENTRIFUGE | MSP Curd | 14-3320 | #7 CON CENTRIFUGE SHARPLE |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | 4 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | NR |  |  |  |  | Clean and flush | flush |  | 2021-12-16 |  |  |  | 16 | 6
MEM-PRO-014-CON-CON-3320 | MSP-#7 CONCENTRATION CENTRIFUGE | MSP Curd | 14-3320-08 | #7 CON CENTRIFUGE OIL PUMP |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | 4 | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | NR | [7 empty] | 2021-12-21 |  |  |  | 16 | 6
MEM-PRO-014-CON-CRE-3363 | MSP-#3 CURD POT GRINDER | MSP Curd | 14-3363 | #3 CURD POT GRINDER |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | NR | [7 empty] | 2021-12-21 |  |  |  | 16 | 6
MEM-PRO-014-CON-CRE-4072 | MSP-#2 CURD POT GRINDER | MSP Curd | 14-4072 | MSP-#2 CURD POT GRINDER |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | bad data | OK | OK | ok | NR | [7 empty] | 2021-12-21 |  |  |  | 16 | 6
MEM-PRO-014-CON-CRE-4073 | MSP-#1 CURD POT GRINDER | MSP Curd | 14-4073 | MSP-#1 CURD POT GRINDER |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | OK | OK | ok | NR | [7 empty] | 2021-12-21 |  |  |  | 12 | 6
MEM-PRO-014-CON-CON-4085 | MSP-#9 CONCENTRATION CENTRIFUGE | MSP Curd | 14-4085 | #9 CON CENTRIFUGE SHARPLE |  | South | OK | OK | OK | OK | OK | OK | 2 | WR | 2 | 3 | 1 | NR | 1 | 2 | 3 | 2 | 1 | 2 | 2 | 3 | 2 | NR |  |  |  |  | Centrifuge input shows strong shaft speed harmonic radial and a dominant 2x harmonic in the axial. Inspect for loose fasteners and looseness as well asdrive train alignment. |  |  | 2021-12-16 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-CON-CON-4085 | MSP-#9 CONCENTRATION CENTRIFUGE | MSP Curd | 14-4085-08 | #9 CON CENTRIFUGE OIL PUMP |  | South | OK | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | 4 | 4 | 4 | OK | 4 | 3 | 4 | OK | OK | ok | NR | [7 empty] | 2021-12-21 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-CON-CRE-4095 | MSP-#4 CURD POT GRINDER | MSP Curd | 14-4095 | MSP-#4 CURD POT GRINDER |  | South | OK | OK | OK | OK | 2 | OK | OK | OK | NR | 3 | OK | OK | 3 | 2 | OK | OK | OK | bad data | 4 | ok | ok | NR |  |  |  |  | Grinder speed vibration in motor. Inspect the unit drivetrain for wear and alignment. Check all | done |  | 2021-12-21 |  |  |  | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-011-PKG-PAK-5304 | MP1B-SURGE BIN ASPIRATION FAN | MSP Dryer Dry | 11-5304-0 | PH1 PACKER SURGE BIN ASP FAN |  | North | NR | OK | 3 | 3 | WR | NR | OK | NR | OK | NR | 3 | 3 | 3 | 4 | 3 | NR | 3 | WR | 4 | 3 | NR | NR |  |  |  |  | Increase in 3x fan speed vibration in the inboard fan bearing. Inspect the units’ fasteners, base, and | 7234222 | #VALUE! | 2021-11-09 |  |  | 6 | 16 | 6
MEM-PRO-011-PKG-PAK-5307 | MP1B-ASPIRATION FILTER FAN | MSP Dryer Dry | 11-5307-0 | MP1B-ASPIRATION FILTER FAN |  | North | NR | OK | NR | OK | OK | NR | OK | NR | NR | NR | ok | OK | NR | ok | OK | NR | OK | NR | NR | NR | NR | NR | [7 empty] | 2021-08-13 |  |  |  | 16 | 6
MEM-PRO-014-SPR-DRY-3608 | MSP-COOLING RING INTAKE FAN | MSP Dryer Dry | 14-3608 | MSP-COOLING RING INTAKE FAN |  | South | NR | OK | 3 | 3 | 3 | WR | OK | NR | OK | OK | 4 | 3 | 3 | 3 | 3 | NR | 3 | 3 | 3 | 1 | 1 | NR |  |  |  |  | Motor has increased 1x RPM vibration at 1.2"/second velocity. Inspect unit for all issues ASAP. | 7277498 |  | 2021-12-23 |  |  | 12 | 16 | 6
MEM-PRO-014-SPR-DRY-3617 | MSP-SPRAY DRYER SE FILTER | MSP Dryer Dry | 14-3617 | DRYER SE CS FILTER BLOWER |  | South | NR | OK | 4 | 4 | 4 | NR | OK | NR | OK | NR | 4 | OK | OK | ok | 4 | NR | OK | OK | NR | 3 | ok | NR |  |  |  |  | The blower outboard horizontal is showing an increased vibration at what looks like 50 orders and the | 7269900 | #VALUE! | 2021-12-22 |  |  | 8 | 4 | 6 |  | drain sample with online filtering and oil coolier
MEM-PRO-014-SPR-DRY-3618 | MSP-SPRAY DRYER EAST EXHAUST FAN | MSP Dryer Dry | 14-3618 | SPRAY DRYER EAST EXHAUST FAN |  | South | OK | OK | 3 | OK | OK | NR | OK | NR | 3 | 3 | 4 | OK | OK | 4 | 3 | NR | 3 | 4 | 4 | 4 | 4 | NR |  |  |  |  | Possible electrical issue in motor due to jump in rotor bar fundamental. Check connections. |  |  | 2021-12-22 |  |  | 12 | 16 | 6
MEM-PRO-014-SPR-DRY-3627 | MSP-SPRAY DRYER NE FILTER | MSP Dryer Dry | 14-3627 | DRYER NE CS FILTER BLOWER |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | NR | 4 | 3 | 3 | 4 | 3 | NR | 4 | 4 | 3 | ok | ok | NR |  |  |  |  | Blower vibrations have dropped. No action required. |  |  | 2021-12-22 |  |  | 8
MEM-PRO-014-SPR-DRY-3634 | MSP-SPRAY DRYER SW FILTER | MSP Dryer Dry | 14-3634 | DRYER SW CS FILTER BLOWER |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | NR | ok | OK | 2 | 3 | 3 | NR | 3 | WR | 3 | 3 | 3 | NR |  |  |  |  | replaced in Jan |  |  | 2021-12-22 |  |  | 8 | 16 | 4 | [21 empty] | uses metal pole
MEM-PRO-014-SPR-DRY-3636 | MSP-SPRAY DRYER WEST EXHAUST FAN | MSP Dryer Dry | 14-3636 | SPRAY DRYER WEST EXHAUST FAN |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | 3 | 3 | 4 | 3 | 4 | NR | 3 | 3 | 3 | 4 | 4 | NR |  |  |  |  | Slight fan 1x RPM axial vibration about the same. Continue to watch. | done |  | 2021-12-22 |  |  | 12 | 16 | 50
MEM-PRO-014-SPR-DRY-3642 | MSP-SPRAY DRYER NW FILTER | MSP Dryer Dry | 14-3642 | DRYER NW CS FILTER BLOWER |  | South | NR | OK | 4 | 4 | 4 | NR | OK | NR | OK | NR | ok | 3 | 3 | 3 | 3 | NR | 3 | 3 | 3 | 4 | 4 | NR |  |  |  |  | Blower speed vibration in motor. Check fasteners and drivetrain alignment. |  |  | 2021-12-22 |  |  | 8 | 16 | 4
MEM-PRO-014-SPR-PRC-3648 | MSP-PRODUCT COLLECTOR | MSP Dryer Dry | 14-3648 | MSP-PRODUCT COLLECTOR BLOWER |  | South | NR | OK | 4 | 4 | 4 | NR | OK | NR | OK | NR | ok | 4 | OK | ok | 3 | NR | ok | ok | NR | ok | ok | NR |  |  |  |  | fasteners, structure, and drive train components. Rated a Class I Defect. |  |  | 2021-12-22 |  |  | 12 | 16 | 4
MEM-PRO-014-SPR-PRC-3649 | MSP-PRODUCT COLLECTOR EXHAUST FAN | MSP Dryer Dry | 14-3649 | PRODUCT COLLECT EXHAUST FAN |  | South | NR | OK | 2 | OK | OK | NR | OK | NR | OK | NR | 2 | 2 | 2 | 3 | 3 | NR | 3 | 3 | 3 | ok | ok | NR | [7 empty] | 2021-12-22 |  |  | 12 | 16 | 50
MEM-PRO-014-SPR-PRC-3655 | MSP-PARTICLE REDUCTION TURBO FAN | MSP Dryer Dry | 14-3655 | PARTICLE REDUCTION TURBO FAN |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | NR | 4 | OK | OK | NR | OK | NR | OK | OK | NR | ok | ok | NR |  |  |  |  | bad data |  |  | 2021-12-22 |  |  | 8 | 16 | 50
MEM-PRO-014-PKG-BLD-3697 | MSP-PACKAGING ASPIRATION FILTER RCVR FAN | MSP Dryer Dry | 14-3697 | FILTER EXHAUST FAN |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | NR | NR | NR | ok | NR |  |  |  |  | sheaves. Check alignment, fasteners, and belt tension. Rated a Class I Defect. Please confirm speeds |  |  | 2021-12-23 |  |  | 1 | 16 | 50
MEM-PRO-014-PKG-BLD-3706 | MSP-ISOLATE SURGE BIN ASPIRATION FAN | MSP Dryer Dry | 14-3706 | ISOLATE SURGE BIN ASP FAN |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 3 | NR | NR | NR | 3 | NR |  |  |  |  | Possible belt and fan vibrations in motor. Check fasteners, structure, and drive train components for wear and alignment | 7257842 | #VALUE! | 2021-12-23 |  |  | 1 | 16 | 50
MEM-PRO-014-PKG-BLD-3710 | MSP-BLENDER - RIBBON | MSP Dryer Dry | 14-3710 | MSP-BLENDER - RIBBON |  | South | NR | OK | NR | OK | OK | NR | OK | NR | OK | OK | 4 | 4 | 4 | ok | 4 | NR | 4 | 4 | 4 | ok | 3 | NR |  |  |  |  | Jump in motor 1x RPM vibration in unit. Check the coupling fill for clumping, and alignment. | 7277499 |  | 2021-12-23 |  |  | 12 | 16 | 50 |  |  | yes | No motor picture
MEM-PRO-014-PKG-BLD-3712 | MSP-BLENDER BIN ASPIRATION FAN | MSP Dryer Dry | 14-3712 | MSP-BLENDER BIN ASP FAN |  | South | NR | NR | NR | NR | NR | NR | OK | NR | OK | OK | 3 | 2 | 4 | 2 | 1 | NR | 1 | NR | NR | NR | 3 | NR |  |  |  |  | Motor vibration has 1x RPM and sub synchromous vibrations. Inspect for defects in drivetrain. | 7277520 |  | 2021-12-23 |  |  | 1 | 16 | 50
MEM-PRO-014-PKG-PAK-3720 | MSP-#1 AZO SCREENER SYSTEM | MSP Dryer Dry | 14-3720 | #1 AZO AUTOP SCREENER SYSTEM |  | South | NR | OK | NR | OK | OK | NR | OK | NR | OK | OK | ok | OK | 4 | NR | OK | NR | OK | OK | NR | ok | 4 | NR |  |  |  |  | Harmonics of 9.4 Hz in motor. Confirm unit shaft speeds. |  |  | 2021-12-23 |  |  | 1 | 16 | 4
MEM-PRO-014-SPR-DRY-3761 | MSP-SPRAY DRYER INLET FAN | MSP Dryer Dry | 14-3761 | MSP-SPRAY DRYER INLET FAN |  | South | NR | OK | NR | OK | OK | NR | OK | NR | OK | OK | 3 | 4 | 3 | 3 | OK | NR | OK | NR | NR | ok | ok | NR |  |  |  |  | A sub synchronous vibration still dominates the data. We suspect a belt, structural or fastener issue. Inspect as time allows. Possible early bearing issue in fan also. Ensure the fan bearings are lubricated. Rated a Class II Defect. |  |  | 2021-12-23 | IB Fan bering Failure 7/21 missed |  | 12 | 12 | 4 | [6 empty] | Yes
MEM-PRO-014-SPR-PRC-4070 | MSP-PRODUCT COLLECTOR TRANSFER BLOWER | MSP Dryer Dry | 14-4070 | PROD COLLECTOR TRANS BLOWER |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | NR | 4 | OK | OK | ok | OK | NR | OK | NR | NR | ok | ok | NR |  |  |  |  | drive train defects |  |  | 2021-12-22 |  |  | 12
MEM-PRO-014-PKG-PAK-4180 | MSP-BLENDER DISCHARGE BLOWER | MSP Dryer Dry | 14-4180 | BLENDER DISCHARGE BLOWER |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | NR | NR | NR | ok | NR |  |  |  |  | speed. Rated a Class I Defect. |  |  | 2021-08-13
MEM-PRO-014-PKG-PAK-4921 | MSP-BAG PACKER VACCUUM PUMP | MSP Dryer Dry | 14-4921 | MSP-BAG PACKER VACCUUM PUMP |  | New South | [26 empty] | fasteners. Rated a Class I Defect. |  |  | 2021-12-23 |  |  | 1 | bar: NR to NR
MEM-PRO-014-SPR-PRC-5212 | MSP-DRY REWORK FAN | MSP Dryer Dry | 14-5212 | REWORK FAN |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | NR | NR | NR | ok | NR | [7 empty] | 2021-12-23
MEM-PRO-014-PKG-PAK-5376 | MSP-BLENDER DISCHARGE BLOWER | MSP Dryer Dry | 14-5376 | BLENDER DIS XFER BLOWER |  | South | NR | OK | NR | OK | OK | NR | OK | NR | OK | OK | ok | OK | OK | ok | OK | NR | OK | OK | NR | 3 | 4 | NR |  |  |  |  | Harmonic data in blower. No action required. |  |  | 2021-12-23 |  |  | 8 | 16 | 43
MEM-PRO-010-SLM-AEQ-5681 | MS2P-SLAM SURGE PUMP #1 | MSP Dryer Wet | 10-5681-0 | SLAM SURGE PUMP #1 |  | New South | [26 empty] | somewhat worn. We only have 3 sets of data to go by. Inspect the unit as time allows for excessive |  |  | 2021-03-04 |  |  |  | 16 | 7 | bar: NR to NR
MEM-PRO-014-IDN-IDF-2981 | MSP-EAST DYNATROL PUMP | MSP Dryer Wet | 14-2981 | MSP-EAST DYNATROL PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | OK | OK | ok | OK | OK | ok | OK | NR | NR | ok | NR | [7 empty] | 2021-12-14 |  |  |  | 16 | 50
MEM-PRO-014-IDN-IDF-3350 | MSP-W. CHILL TANK PUMP | MSP Dryer Wet | 14-3350 | MSP-WEST CHILL TANK PUMP |  | South | NR | NR | OK | NR | OK | NR | NR | NR | NR | OK | OK | OK | OK | ok | OK | OK | OK | NR | NR | NR | ok | NR | [7 empty] | 2021-12-14 |  |  |  | 8 | 4
MEM-PRO-014-IDN-IDF-3352 | MSP-E. CHILL TANK PUMP | MSP Dryer Wet | 14-3352 | MSP-EAST CHILL TANK PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | OK | OK | ok | NR | NR | OK | OK | NR | NR | ok | NR |  |  |  |  | be operating out of the correct part of the performance curve. Rated a Class I Defect. |  |  | 2021-12-23 |  |  |  | 16 | 3
MEM-PRO-014-IDN-HYS-3383 | MSP-NAOH PUMP TO HYDROLYSIS TANKS | MSP Dryer Wet | 14-3383 | NAOH PUMP-HYDROLYSIS TANKS |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | OK | NR | NR | NR | ok | NR | [7 empty] | 2021-12-23 |  |  | 4 | 16 | 50
MEM-PRO-014-UTL-CSY-3404 | MSP-IDN CAUSTIC SUPPLY PUMP | MSP Dryer Wet | 14-3404 | MSP-IDN CAUSTIC SUPPLY PUMP |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | ok | ok | ok | NR | NR | ok | NR |  |  |  |  | Pump bearing are also in distress. Check and inspect the pump bearings for adequate lubrication. |  |  | 2021-12-14 |  |  | 4 | 16 | 4
MEM-PRO-014-IDN-IDF-3425 | MSP-E IDN TANK PUMP | MSP Dryer Wet | 14-3425 | MSP-EAST IDN TANK PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | 4 | 4 | 3 | OK | ok | ok | 1 | NR | ok | ok | NR |  |  |  |  | The pump vibrations have jumped up almost exponentially. We believe the pump could fail at any time. Replace the pump, check all fasteners and coupling, align ASAP. Rated a Class IV Defect. |  |  | 2021-12-14
MEM-PRO-014-BGY-FCS-3461 | MSP-S BOGEY CONDENSATE PUMP | MSP Dryer Wet | 14-3461 | SOUTH BOGEY CONDENSATE PUMP |  | South | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | OK | OK | OK | ok | OK | OK | OK | OK | NR | NR | 4 | NR |  |  |  |  | SLIGHT 1X IN PUMP CHECK BOLTS AND COUPLING |  |  | 2021-12-14 |  |  | 8 | 16 | 7
MEM-PRO-014-BGY-FCS-3471 | MSP-S BOGEY VACUUM PUMP | MSP Dryer Wet | 14-3471 | SOUTH BOGEY VACUUM PUMP |  | South | NR | OK | OK | OK | OK | NR | NR | NR | NR | OK | OK | 4 | OK | ok | OK | OK | OK | OK | NR | NR | ok | NR |  |  |  |  | Class II Defect. |  |  | 2021-12-14 |  |  | 8 | 16 | 7 | [6 empty] | Yes
MEM-PRO-014-BGY-FCS-3475 | MSP-S BOGEY VACUMMIZER DISCHARGE PUMP | MSP Dryer Wet | 14-3475 | S BOGEY VACUUMIZER DIS PUMP |  | South | NR | OK | OK | OK | OK | NR | NR | NR | NR | 3 | 3 | 3 | 3 | 2 | OK | OK | 4 | ok | NR | NR | 4 | NR |  |  |  |  | CAVITATION |  |  | 2021-12-14 |  |  | 8 | 16 | 7 | [6 empty] | Yes
MEM-PRO-014-BGY-FCS-3534 | MSP-N BOGEY CONDENSATE PUMP | MSP Dryer Wet | 14-3534 | NORTH BOGEY CONDENSATE PUMP |  | South | NR | OK | OK | OK | NR | NR | OK | NR | NR | OK | OK | 4 | 4 | 2 | OK | OK | OK | OK | NR | NR | ok | NR |  |  |  |  | The motor outboard vibration data shows a dominant vibration at just over 10 Hz. We are not sure what this is, but it has been in past data spectrums. We assume it is sub synchronous, so it could be a resonance, which is sometimes seen in vertical pumps. The overall peak velocity is almost 0.5”/second. | done |  | 2021-12-14 |  |  | 8 | 16 | 7
MEM-PRO-014-BGY-FCS-3539 | MSP-N BOGEY VACUUM PUMP | MSP Dryer Wet | 14-3539 | NORTH BOGEY VACUUM PUMP |  | South | NR | OK | OK | NR | NR | NR | OK | NR | NR | OK | OK | OK | OK | ok | OK | OK | OK | OK | NR | NR | ok | NR | [7 empty] | 2021-12-14 |  |  | 8 | 32 | 6
MEM-PRO-014-BGY-FCS-3550 | MSP-N BOGEY VACUMMIZER DISCHARGE PUMP | MSP Dryer Wet | 14-3550 | N BOGEY VACUUMIZER DIS PUMP |  | South | NR | OK | OK | OK | NR | NR | OK | NR | OK | OK | OK | OK | 4 | 4 | 4 | 4 | 4 | 3 | NR | NR | 4 | NR |  |  |  |  | CAVITATION | 7262397 | #VALUE! | 2021-12-14 |  |  | 8 | 16 | 7
MEM-PRO-014-IDN-HYS-3562 | MSP-N HYDROLYSIS PUMP | MSP Dryer Wet | 14-3562 | NORTH HYDROLYSIS TANK PUMP |  | South | NR | NR | OK | NR | OK | NR | NR | NR | NR | OK | 3 | 3 | 4 | NR | NR | NR | NR | NR | NR | NR | ok | NR |  |  |  |  | Motor axial vibration is just under 0.5”/second velocity peak at near 51 Hz. Inspect the coupling and alignment as time allows. Rated a Class I Defect. | done |  | 2021-12-23 |  |  |  | 16 | 7
MEM-PRO-014-IDN-HYS-3572 | MSP-S HYDROLYSIS PUMP | MSP Dryer Wet | 14-3572 | SOUTH HYDROLYSIS TANK PUMP |  | South | NR | NR | NR | NR | OK | NR | NR | NR | NR | NR | OK | NR | OK | NR | NR | OK | OK | NR | NR | NR | ok | NR | [7 empty] | 2021-12-14 |  |  |  | 16 | 7
MEM-PRO-014-UTL-PRW-4216 | MSP-90 DEG WASHDOWN WTR BOOSTER PUMP | MSP Dryer Wet | 14-4216 | 90 DEG WASHDOWN WTR BSTR PMP |  | New South | [26 empty] | Rated a Class III Defect. |  |  | 2021-12-14 |  |  | 4 | 16 | 7 | bar: NR to NR
MEM-PRO-014-IDN-IDF-4710 | MSP-CAUSTIC ADJUST DISCHARGE PUMP | MSP Dryer Wet | 14-4710 | CAUSTIC ADJUST DISCH PUMP |  | New South | [29 empty] | #N/A |  |  | 4 | bar: NR to NR
MEM-PRO-014-UTL-CSY-4714 | MSP-PASTEURIZATION TANK DISCHARGE PUMP | MSP Dryer Wet | 14-4714 | PASTEURZTION TANK DISC PUMP |  | New South | [29 empty] | 2021-08-11 |  |  | 6 | bar: NR to NR
MEM-PRO-014-FED-SLT-2201 | MSP - FEED SLUDGE XFER CONVEYOR | MSP Feed Dryer | 14-2201 | FEED SLUDGE XFER CONVEYOR |  | New South | [26 empty] | the fan wheel. Rated a Class I Defect. |  |  | 2021-12-14 |  |  | 6 | 16 | 7 | bar: NR to NR
MEM-PRO-014-FED-FED-2297 | MSP-RECYL FLW ELE TO PDL MXR | MSP Feed Dryer | 14-2297 | MSP-RECYL FLW ELE TO PDL MXR |  | New South | [29 empty] | 2021-12-14 |  |  | 8 | 32 | 7 | bar: NR to NR
MEM-PRO-014-FED-FED-3800 | MSP-DOUBLE PADDLE MIXER | MSP Feed Dryer | 14-3800 | DOUBLE PADDLE MIXER CONVEYOR |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | 3 | 3 | OK | 3 | 2 | NR | ok | ok | 3 | 3 | 3 | 3 | NR |  |  |  |  | INSPECT ALL ASPECTS OF MIXER FOR DEFECTS AND ALIGNMENT | 7228130 | #VALUE! | 2021-12-14 |  |  | 12 | [27 empty] | 0.60345
MEM-PRO-014-FED-FED-3806 | MSP-FEED DRYER DISCH BLOWER | MSP Feed Dryer | 14-3806 | FEED DRYER DISCH TRAN BLOWER |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | OK | 3 | OK | OK | ok | NR | ok | ok | ok | 3 | 3 | 4 | NR |  |  |  |  | SOME BLOWER WEAR | 7267881 | #VALUE! | 2021-12-14 |  |  | 4 | 16 | 6
MEM-PRO-014-FED-FED-3827 | MSP-FEED DRYER TO FEED LOADOUT BLOWER | MSP Feed Dryer | 14-3827 | FD TO FEED LOADOUT BLOWER |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | OK | OK | OK | OK | ok | NR | ok | ok | ok | ok | ok | ok | NR |  |  |  |  | loading. Check the operational parameters and the unit in general. Rated a Class II Defect. |  |  | 2021-12-14 |  |  | 6
MEM-PRO-014-FED-FED-3828 | MSP-FEED DRYER RECYCLE BLOWER | MSP Feed Dryer | 14-3828 | FEED DRYER RECYCLE BLOWER |  | South | NR | OK | NR | OK | OK | NR | NR | NR | 3 | 3 | 3 | OK | 3 | 4 | NR | WR | 3 | 3 | 3 | 3 | 3 | NR |  |  |  |  | DATA SUGGEST WEAR IN THE BLOWER. INSPECT UNIT AND CHECK FOR LOOSENESS | 7226601 | #VALUE! | 2021-12-14 |  |  | 6
MEM-PRO-014-FED-FED-3832 | MSP-F.D. RECYCLE SCREW CONVEYOR | MSP Feed Dryer | 14-3832 | F.D. RECYCLE SCREW CONVEYOR |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | OK | OK | OK | 4 | ok | NR | ok | ok | 4 | ok | ok | ok | NR | [7 empty] | 2021-12-14 |  |  | 6
MEM-PRO-014-FED-FED-3836 | MSP-FEED DRYER DRY FEED RECEIVER ASP FAN | MSP Feed Dryer | 14-3836 | DRY FEED RECEIVER ASP FAN | speed | South | NR | OK | NR | OK | 3 | NR | NR | NR | OK | OK | 3 | OK | OK | 3 | NR | 3 | 3 | 3 | 3 | 3 | 3 | NR |  |  |  |  | Motor 1x vibrations are lower but still high. Fan axial has risen. Check bolts, belts, and alignment. | 7259666 | #VALUE! | 2021-12-14 |  |  | 4
MEM-PRO-014-FED-FED-3843 | MSP-BURNER #1 PROCESS FAN | MSP Feed Dryer | 14-3843 | S INLET BURNER 1 PROCESS FAN |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | 4 | 4 | OK | 4 | 3 | NR | ok | ok | 4 | 4 | ok | 4 | NR |  |  |  |  | Increased acceleration in fan bearings. Ensure proper lubrication and inspect. |  |  | 2021-12-14 |  |  | 8 | 8 | 7
MEM-PRO-014-FED-FED-3844 | MSP-BURNER #1 COMBUSTION FAN | MSP Feed Dryer | 14-3844 | S BURNER #1 COMBUSTION FAN | rpm | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | OK | 4 | OK | OK | 4 | NR | NR | 4 | 4 | 4 | ok | 4 | NR |  |  |  |  | 1x RPM vibration in fan bearings. Clean and inspect the fan wheel and sheave. Check all fasteners and belts too. |  |  | 2021-12-14 |  |  | 6 | 16 | 7
MEM-PRO-014-FED-FED-3847 | MSP-BURNER #2 PROCESS FAN | MSP Feed Dryer | 14-3847 | N BURNER 2 PROCESS INLET FAN |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | OK | 4 | OK | 4 | 4 | NR | NR | ok | ok | ok | ok | 3 | NR |  |  |  |  | Strong vibration at near 28 Hz. Inspect and clean the fan wheel. Check for wear and run out in drive train. | 7274548 |  | 2021-12-14 | Fan wheel had a crack 1-11-22 |  | 8 | 16 | 7 |  |  | yes | 1770
MEM-PRO-014-FED-FED-3848 | MSP-BURNER #2 COMBUSTION FAN | MSP Feed Dryer | 14-3848 | N BURNER #2 COMBUSTION FAN |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | OK | 3 | OK | OK | ok | NR | NR | ok | ok | ok | ok | ok | NR |  |  |  |  | defects. Check the drive train components for wear, eccentricity, and alignment. Clean and inspect the |  |  | 2021-12-14 |  |  | 6 | 16 | 7
MEM-PRO-014-FED-FED-3863 | MSP-FEED DRYER EXHAUST FAN | MSP Feed Dryer | 14-3863 | MSP-FEED DRYER EXHAUST FAN |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | 4 | 3 | OK | OK | 3 | NR | ok | ok | 4 | 4 | ok | 4 | NR |  |  |  |  | Subsynchronous vibration could be a belt issue. Inspect as time allows. |  |  | 2021-12-14 |  |  | 6 | 8 | 7
MEM-PRO-014-FED-FED-3866 | MSP-FEED DRYER BAGHOUSE DISC SCREW | MSP Feed Dryer | 14-3866 | FD DCE BAGHOUSE DISC SCREW |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | OK | OK | OK | OK | ok | NR | ok | ok | ok | ok | ok | ok | NR |  |  |  |  | vibration and a sub-synchronous vibration in the motor data. Inspect the base, fasteners, and structure |  |  | 2021-12-14 |  |  | 6 | 16 | 7
MEM-PRO-014-FED-FED-3868 | MSP-FEED DRYER BAGHOUSE DISC BLOWER | MSP Feed Dryer | 14-3868 | FD DCE BAGHOUSE DISC BLOWER |  | South | NR | OK | NR | OK | OK | NR | NR | NR | OK | OK | OK | OK | OK | ok | NR | ok | ok | ok | ok | ok | ok | NR |  |  |  |  | for defects. Check the drive train components for wear, eccentricity, and alignment. Clean and inspect |  |  | 2021-12-14 |  |  | 6 | 16 | 7
MEM-PRO-014-CIP-SAC-4007 | MSP-CIP WATER RINSE TANK HEATER PUMP | MSP Feed Dryer | 14-4007 | CIP W RINSE TANK HEATER PUMP |  | South | NR | NR | NR | 1 | 1 | NR | 4 | NR | 4 | OK | 3 | 3 | 3 | 3 | 3 | 3 | 3 | ok | ok | ok | ok | NR |  |  |  |  | The inboard pump vibration data is dominated by 1x and 2x RPM vibrations. Inspect the pump fasteners, base, structure, coupling, and shaft alignment. Rated a Class II Defect. | done |  | 2021-12-14 |  |  | 2 | 16 | 7
MEM-PRO-014-CIP-CAC-4027 | MSP-CIP RINSE TANK FLOW VALVE TO 4027 | MSP Feed Dryer | 14-4027 | MSP-CIP SUPPLY PUMP/WET-IN |  | New South | [26 empty] | fan wheel. Rated a Class I Defect. |  |  | #N/A |  |  |  | 8 | 7 | bar: NR to NR
MEM-PRO-014-CIP-CAC-4028 | MSP-CIP RINSE TANK FLOW VALVE TO 4028 | MSP Feed Dryer | 14-4028 | MSP-CIP SUPPLY FEED PUMP |  | New South | [29 empty] | #N/A |  |  |  | 16 | 7 | bar: NR to NR
MEM-PRO-014-CIP-DAC-4050 | MSP-CIP SUPPLY PUMP TO DRYER #1 | MSP Feed Dryer | 14-4050 | CIP SUPPLY PUMP TO DRYER #1 |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 3 | NR | NR | NR | NR | ok | NR | NR | NR | ok | NR |  |  |  |  | Need to check to see if setup in database correctly |  |  | 2021-08-17 |  |  | 2
MEM-PRO-014-CIP-DAC-4051 | MSP-CIP SUPPLY PUMP TO DRYER #2 | MSP Feed Dryer | 14-4051 | MSP #2 CIP FEED PUMP |  | New South | [29 empty] | 2021-03-10 |  |  | 2 | bar: NR to NR
MEM-PRO-014-UTL-PRW-4203 | MSP-HOT WATER PUMP TO H-HEATER | MSP Feed Dryer | 14-4203 | HOT WATER PUMP TO H-HEATER |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 4 | NR | 3 | 4 | 3 | 3 | 3 | NR |  |  |  |  | Pump vibrations are near 1”/second velocity peak. Check and inspect the unit fasteners, coupling, alignment, and base. | 7259667 | #VALUE! | 2021-12-14 |  |  |  | 16 | 7 | [6 empty] | Yes
MEM-PRO-014-UTL-PRW-4208 | MSP-90 DEG F PROCESS WTR PUMP | MSP Feed Dryer | 14-4208 | 90 DEG F PROCESS WTR PUMP |  | South | NR | 3 | NR | NR | NR | NR | NR | NR | NR | OK | NR | 4 | NR | NR | OK | NR | ok | 2 | 2 | ok | ok | NR |  |  |  |  | Pump vibration shows 1x, and 2x RPM vibration with the 2x dominant. Vibrations have slightly |  |  | 2021-12-14 | #N/A |  | 4 | 16 | 7 | [6 empty] | Yes
MEM-PRO-014-UTL-PRW-4209 | MSP-90 DEG PROCESS STANDBY WTR PUMP | MSP Feed Dryer | 14-4209 | 90D PROCESS STANDBY WTR PUMP |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 3 | NR | 3 | 3 | 2 | ok | 2 | NR |  |  |  |  | Pump vibration still shows 1x, 2x, and 3x RPM vibrations with the 2x dominant. Overall for pump input | 7274550 |  | 2021-12-14 |  |  | 4 | 16 | 7
MEM-PRO-010-UTL-PRW-2497 | MSS-MN PLT NORTH 90 DEG WTR TK C PUMP | North Util | 10-2497-0 | 90 D WTR TK C SUPPLY PUMP #2 |  | North | OK | OK | NR | OK | OK | 4 | OK | NR | 4 | OK | ok | OK | OK | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14
MEM-PRO-010-UTL-PRW-2499 | MSS-MN PT WASHDOWN BOOSTER PUMP | North Util | 10-2499-0 | 90 D WASHDOWN BOOSTER PUMP |  | North | OK | OK | OK | OK | 4 | 3 | OK | NR | 3 | 3 | 3 | 3 | OK | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  | Pump has high axial 2 x rpm vibration. This may be caused by excessive shaft run-out of the pump shaft, misalignment, or coupling issue. | done |  | 2021-12-14
MEM-PRO-010-UTL-IAS-2600 | MSS-300 Ton #7 AIR COMPRESSOR 50 HP | North Util | 10-2600-0 | #7 AIR COMPRESSOR 50 HP |  | North | NR | OK | OK | OK | OK | NR | OK | NR | OK | OK | ok | OK | OK | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14
MEM-PRO-010-GRD-S3G-6382 | S 300T TRANSFER BLOWER | 300 Ton | 10-6382-0 | S 300T BYPASS TRANS BLOWER |  | North | NR | OK | OK | NR | OK | OK | NR | NR | NR | NR | NR | OK | NR | NR | ok | ok | NR | ok | ok | ok | NR | NR |  |  | NR |  |  |  |  | 2021-11-08 |  |  | 4
MEM-PRO-010-GRD-S3G-6417 | MSS-300T S. GRINDER UT62 | 300 Ton | 10-6417-0 | MSS-300T SOUTH GRINDER UT62 |  | North | OK | OK | OK | OK | 4 | 4 | OK | NR | 3 | 3 | 3 | 2 | 2 | 3 | 2 | 3 | 3 | ok | ok | ok | 3 | NR |  |  | 3 | Grinder is showing signs of bearing defects. Still low level right now. Prepare to fix during next TAR. | Grinder is showing signs of bearing defects. Still low level right now. Prepare to fix during next TAR. | 7274534 |  | 2021-12-16 |  |  |  | 16 | 4
MEM-PRO-010-GRD-N3G-6421 | MSS-300T N GRINDER UT62 | 300 Ton | 10-6421-0 | MSS-300T NORTH GRINDER UT62 |  | North | OK | OK | OK | OK | OK | OK | OK | NR | 2 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 3 | 3 | NR |  |  | 3 | Grinder still has high vertical vibration. High 1 x rpm indicates possible imbalance. Also ensure all fasteners are tight. Check sheaves for face run-out and misalignment as time allows. | Grinder still has high vertical vibration. High 1 x rpm indicates possible imbalance. Also ensure all fasteners are tight. Check sheaves for face run-out and misalignment as time allows. | 7271703 | #VALUE! | 2021-12-16 |  |  | 1 | 8 | 25
MEM-PRO-010-GRD-S3G-7907 | MSS-300T W GRD FILT REC'R ASP FAN | 300 Ton | 10-7907-0 | 300T W GRD FILT RECR ASP FAN |  | North | OK | NR | OK | OK | OK | OK | OK | NR | 4 | OK | ok | OK | OK | 2 | 2 | 3 | NR | 3 | 3 | 3 | 3 | NR |  |  | 3 | Fan inboard has high vibration near 1 x fan rpm. This appears to be resonance. | Fan inboard has high vibration near 1 x fan rpm. This appears to be resonance. | 7262305 | #VALUE! | 2021-12-16 |  |  |  | 8 | 36 | [6 empty] | Yes
MEM-PRO-010-GRD-N3G-7917 | MSS-300T E GRD FILT REC'R ASP FAN | 300 Ton | 10-7917-0 | 300T E GRD FILT RECR ASP FAN |  | North | OK | NR | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | OK | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  | 1 | 8 | 4 | [6 empty] | Yes
MEM-PRO-010-UTL-CWS-8505 | MSS-W PROCESS COOLING TOWER W PUMP | North Util | 10-8505-0 | COOLING TOWER W CIRC PUMP #3 |  | North | OK | OK | OK | OK | OK | OK | OK | NR | NR | NR | NR | OK | OK | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 4
MEM-PRO-010-UTL-CWS-8506 | MSS-W PROCESS COOLING TOWER E PUMP | North Util | 10-8506-0 | COOLING TOWER E CIRC PUMP #4 |  | North | OK | NR | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | OK | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 4
MEM-PRO-010-UTL-CWS-8520 | MSS-EAST UTILITY COOLING TOWER | North Util | 10-8520-0 | EAST COOLING TOWER FAN |  | North | NR | NR | OK | OK | OK | repair | repair | repair | repair | repair | repair | repair | repair | repair | repair | repair | repair | repair | repair | repair | NR | NR |  |  | NR |  | Need to fix wires |  |  | 2020-08-07 |  |  | 4 | 16 | 4
MEM-PRO-010-UTL-CWS-8525 | MSS-E UTILITY COOLING TOWER EAST PUMP | North Util | 10-8525-0 | COOLING TOWER E CIRC PUMP #1 |  | North | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | OK | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 4
MEM-PRO-010-UTL-CWS-8530 | MSS-E UTILITY COOL TOWER WEST PUMP | North Util | 10-8530-0 | E COOL TOWER W CIRC PUMP #2 |  | North | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | OK | NR | ok | ok | ok | ok | ok | 1 | 1 | NR |  |  | NR | IFF was working on pump when I checked these pumps this month. Looks like coupling shredded. Ensure good alignment and recheck vib. | Motor still has high 1 x vibration. Check couplings and fastnerners ASAP! | 7269646 |  | 2021-12-14 |  |  |  | 8 | 4
MEM-PRO-010-UTL-CHS-9305 | Main Plant Chill Water Pump #1 | P3 Curd A | 10-9305-0 | West Chilled Water Pump #1 |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 16 | 42
MEM-PRO-010-UTL-CHS-9306 | Main Plant Chill Water Pump #2 | P3 Curd A | 10-9306-0 | CENTER CHILLED WTR PMP |  | New North | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 16 | 4
MEM-PRO-010-UTL-CHS-9307 | Main Plant Chill Water Pump #3 | P3 Curd A | 10-9307-0 | East Chill Water Pump #3 |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | NR | NR | NR | NR | NR | NR | NR | NR | NR |  |  | NR |  |  |  |  | 2021-03-08 |  |  |  | 16 | 4
MEM-PRO-011-CHL-CCS-0341 | MP1-#1 CHILL TANK DISCHARGE PUMP | P1 Curd | 11-0341 | #1 CHILL TANK DISCHARGE PUMP |  | North | OK | NR | NR | OK | OK | OK | NR | NR | OK | NR | ok | OK | NR | NR | NR | NR | OK | OK | NR | ok | NR | NR |  |  | NR |  |  |  |  | 2021-11-09 |  |  | 3 | 16 | 4
MEM-PRO-011-XTR-1EX-0714 | DECANTER - 1ST EXT EAST | P1 Curd | 11-0714 | DECANTER 1st EXT EAST NX438 |  | North | OK | NR | 3 | 3 | 2 | 2 | NR | NR | 1 | 1 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | NR |  |  | 1 | Main motor still showing some bearing issues. Back drive motor also has SIGNIFICANT 2 x rpm vibration. Inspect coupling and alignment of back drive motor ASAP. Main drive motor also needs replacing ASAP. | Main motor still showing some bearing issues. Back drive motor also has SIGNIFICANT 2 x rpm vibration. Inspect coupling and alignment of back drive motor ASAP. Main drive motor also needs replacing ASAP. | 7267341 | #VALUE! | 2021-12-16 |  |  | 4 | 8 | 4
MEM-PRO-011-XTR-3EX-0715 | DECANTER - 3RD EXT | P1 Curd | 11-0715 | DECANTER-3RD EXT NX438 |  | North | OK | NR | 4 | 3 | 3 | 3 | NR | NR | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 1 | NR |  |  | 1 | Back drive motor has had SIGNIFICANT INCREASE in vibration FOR THE PAST TWO MONTHS . Looks like a coupling and or loose fastener issue. Inspect all fasteners, couplings, and alignment ASAP!!!! | Back drive motor has had SIGNIFICANT INCREASE in vibration FOR THE PAST TWO MONTHS . Looks like a coupling and or loose fastener issue. Inspect all fasteners, couplings, and alignment ASAP!!!! | 7267340 | #VALUE! | 2021-12-16 |  |  |  | 8 | 4
MEM-PRO-011-SPR-DRY-1003 | MP1-NORTH DRYER INLET FAN | P1 Dryer | 11-1003 | MP1-NORTH DRYER INLET FAN |  | North | NR | OK | OK | OK | 3 | NR | NR | NR | OK | OK | ok | OK | ok | NR | ok | 3 | ok | ok | ok | ok | NR | NR |  |  | OK |  |  |  |  | 2021-11-10 |  |  | 6 | 8 | 4
MEM-PRO-011-SPR-DRY-1021 | MP1-NE CSX COLLECTOR BLOWBACK FAN MOTOR | P1 Dryer | 11-1021 | MP1-NE BLOWBACK FAN MOTOR |  | North | NR | OK | OK | OK | 4 | OK | NR | ok | OK | 3 | 3 | 3 | 3 | 3 | 3 | 3 | repair | repair | repair | repair | NR | NR |  |  | NR |  | Equipment was down this survey however, the following likely still applies: Motor has elevated 1 x rpm vibration at the motor verticals. This is likely due to imbalance. It is difficult to field balance these units due to flexible base and inadequate fasteners to the concrete. It is recommended to replace fan wheel with newly dynamically balance wheel or remove this wheel and dynamically balance the wheel in shop during a downtime. Rated as a CLASS II defect. | done |  | 2021-03-09 |  |  | 6 | 8 | 4
MEM-PRO-011-SPR-DRY-1035 | S.D. NORTH EXHAUST FAN | P1 Dryer | 11-1035 | S.D. NORTH EXHAUST FAN |  | North | NR | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | 3 | 2 | 3 | 3 | 2 | NR | NR |  |  | OK | Looked good this month. | Fan vibration has increased. This fan has had issues with build-up causing high vibration. Fan bearings are also showing signs of internal looseness. Clean fan soon and check fan bearings for looseness and wear. | 7267338 | #VALUE! | 2021-11-10 |  |  | 6 | 16 | 4
MEM-PRO-011-SPR-DRY-1041 | MP1-NW CSX BLOWBACK FAN | P1 Dryer | 11-1041 | MP1-NW CSX BLOWBACK FAN |  | North | NR | OK | OK | OK | 4 | OK | NR | ok | 3 | 1 | 3 | 3 | 3 | 3 | ok | ok | ok | ok | ok | ok | NR | NR |  |  | OK |  | Equipment was down this survey however, the following likely still applies: This unit looks much better after shop balancing the wheel. There is still some vertical vibration which is likely due to the base not being anchored properly to the concrete. New anchors should be inserted and epoxied into the concrete and fastened properly. |  |  | 2021-11-10 |  |  |  | 16 | 28
MEM-PRO-011-SPR-DRY-1061 | MP1-SE CSX BLOWBACK FAN MOTOR | P1 Dryer | 11-1061 | MP1-SE BLOWBACK FAN MOTOR |  | North | NR | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | NR | NR | ok | ok | ok | ok | ok | ok | NR | NR |  |  | OK |  |  |  |  | 2021-11-10
MEM-PRO-011-SPR-DRY-1075 | MP1-NORTH CENTER EXHAUST FAN | P1 Dryer | 11-1075 | P1-SOUTH EXHAUST FAN (NC) |  | North | NR | OK | OK | OK | OK | OK | NR | NR | OK | OK | 3 | 3 | 3 | ok | ok | ok | ok | ok | ok | WR | NR | NR |  |  | OK |  | clean wheel | 7268838 |  | 2021-11-10 |  |  | 6 | 8 | 4 | [6 empty] | Yes
MEM-PRO-011-SPR-DRY-1081 | MP1-SW CSX BLOWBACK FAN | P1 Dryer | 11-1081 | MP1-SW CSX BLOWBACK FAN |  | North | NR | OK | OK | OK | 4 | OK | NR | NR | 3 | OK | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | NR | NR |  |  | OK | Looks good since TAR repairs! | Motor data continues to show rpm harmonics which indicate mechanical looseness either in the motor fits or fan hub fit. Base bolts being loose can also cause this type of vibration. Fan is also showing signs of imbalance. Inspect motor/fan for looseness and balance as scheduling allows. | 7233081 | #VALUE! | 2021-11-10 |  |  | 6 | 8 | 5 | [6 empty] | Yes
MEM-PRO-011-SPR-PRC-1098 | S.D. PARTICLE SIZING FAN | P1 Dryer | 11-1098 | S.D. PARTICLE SIZING FAN |  | New North | [24 empty] | OK |  |  |  |  | 2021-11-10 |  |  | 4 | 24 | 4 | bar: NR to NR
MEM-PRO-011-SPR-PRC-1103 | MP1B-PROD COLLECTOR EXHAUST FAN | P1 Dryer | 11-1103 | PROD COLLECTOR EXHAUST FAN |  | North | NR | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | 3 | 3 | 3 | 2 | 2 | 2 | ok | NR |  |  | OK |  | motor looks much better | 7255474 | #VALUE! | 2021-12-08 |  |  | 6 | 8 | 5 | [6 empty] | Yes
MEM-PRO-011-SPR-BRN-1138 | MP1-COOLING RING FAN | P1 Dryer | 11-1138 | MP1-COOLING RING FAN |  | North | NR | OK | OK | 3 | OK | 3 | NR | NR | 4 | 2 | 2 | 2 | OK | ok | ok | ok | ok | ok | ok | ok | NR | NR |  |  | OK |  | OVERALL VIBRATION AT THE OUTBOARD FAN BEARING HAS INCREASED TO OVER 1. IPS. Dominant vibration appears to be sub-synchronous and may be belt related. Motor has a high 1 x motor rpm axial vibration fan bearings appear to have fan rpm harmonics. This indicates severe looseness of the fan bearings. Fan bearings, sheaves, and belt need inspection ASAP. Rated as a CLASS III defect. | done |  | 2021-11-10 | Belt issue found | We had WO in before failure on 8/3/20 | 6 | 8 | 5 | [6 empty] | Yes
MEM-PRO-011-PKG-BLD-1201 | MP1B-PROD COLL XFER BLOWER | P1 Curd | 11-1201 | MP1B-PROD COLL XFER BLOWER |  | New North | [24 empty] | NR |  |  |  |  | #N/A |  |  | 5 | 8 | 5 | [6 empty] | Yes | bar: NR to NR
MEM-PRO-011-WEI-WIS-4075 | MP1-LIME BIN 7B RJ BLOWBACK FAN | P1 Curd | 11-4075-0 | LIME BIN 7B RJ BLOWBACK FAN |  | New North | [24 empty] | NR |  |  |  |  | #N/A |  |  |  | 16 | 49 | bar: NR to NR
MEM-PRO-011-WEI-WIS-4140 | MP1-ISOLATE WET-IN TUBE PUMP | P1 Curd | 11-4140-0 | MP1-ISOLATE WET-IN TUBE PUMP |  | North | OK | NR | NR | OK | OK | OK | NR | NR | 3 | OK | ok | OK | 3 | ok | ok | ok | ok | ok | ok | 3 | ok | NR |  |  | OK |  | looks good after TAR repair! Good job! |  | #VALUE! | 2021-12-16 | May need to replace base add to list. |  | 4
MEM-PRO-011-XTR-1EX-4170 | MP1-1ST EXTRACTION TANK DISCHARGE PUMP | P1 Curd | 11-4170-0 | 1ST EXT TANK DISCHARGE PUMP |  | North | OK | OK | NR | OK | 2 | 2 | NR | NR | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 3 | ok | NR |  |  | OK |  | looks good after TAR repair! Good job! |  | #VALUE! | 2021-12-15 |  |  | 4 | 8 | 4
MEM-PRO-011-XTR-2EX-4265 | MP1-2ND EXTRACTION FEED POT DISCH PUMP | P1 Curd | 11-4265-0 | 2ND EXT FEED POT DISCH PUMP |  | North | OK | OK | NR | 4 | 4 | 4 | NR | NR | 4 | OK | ok | OK | ok | ok | ok | NR | ok | ok | ok | ok | ok | NR |  |  | OK |  | Be prepared to replace in the future. |  |  | 2021-12-16 |  |  | 12 | 33 | 5 |  | drain sample with online filtering and oil coolier |  |  |  |  | Yes
MEM-PRO-011-MEB-CLF-4280 | MP1-CLARIFIED EXTRACT DISCHARGE PUMP | P1 Curd | 11-4280-0 | CLARIFIED EXTRACT DISCH PUMP |  | North | OK | OK | NR | OK | OK | OK | NR | NR | NR | OK | ok | OK | NR | ok | ok | NR | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  | 6 | 16 | 5
MEM-PRO-011-WSH-CWH-4330 | MP1-C30 FEED TANK DISCH PUMP | P1 Curd | 11-4330-0 | MP1-C30 FEED TANK DISCH PUMP |  | North | OK | OK | NR | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | NR | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  | 6 | 16 | 5
MEM-PRO-011-XTR-2EX-4340 | MP1-2ND EXTRACTION CENTRIFUGE | P1 Curd | 11-4340-0 | MP1-2ND EXT CENTRIFUGE P5000 |  | North | OK | NR | OK | 4 | 4 | 3 | NR | NR | 4 | 3 | 3 | 2 | 3 | ok | ok | NR | repair | repair | ok | ok | ok | NR |  |  | OK |  | Overall vibration is much better in the back bearings. 1 x rpm is also lower in the centrifuge. Data still shows some 2 and 3 x rpm in the axial direction. This may indicate some shaft run-out or misaligned/cocked bearings. | done |  | 2021-12-16 |  |  | 8 | 16 | 5
MEM-PRO-011-XTR-2EX-4340 | MP1-2ND EXTRACTION CENTRIFUGE | P1 Curd | 11-4340-1 | 2ND EXT CENTRIFUGE P5000 OIL |  | North | OK | NR | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | NR | NR | NR | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  | 8 | 16 | #N/A
MEM-PRO-011-XTR-1EX-4341 | MP1-1ST EXTRACTION CENTRIFUGE | P1 Curd | 11-4341-0 | MP1-1ST EXT CENTRIFUGE 5400 |  | North | OK | NR | OK | OK | OK | 3 | NR | NR | 4 | OK | ok | OK | 2 | 2 | 2 | 2 | 2 | 3 | ok | ok | ok | NR |  |  | OK |  | Vibration levels are lower this month. Motor DE bearing data is still showing a non-synchronous peak at 5.2 orders which is likely a harmonic of ball spin frequency. Peakvue and 1-20 kHz trend data are also showing indications of a bearing issue. |  |  | 2021-12-16 | lost gearbox and jackshaft on May 29th |  | 8 | 38 | 5 |  | drain sample with online filtering and oil coolier |  |  |  |  | Yes
MEM-PRO-011-XTR-1EX-4341 | MP1-1ST EXTRACTION CENTRIFUGE | P1 Curd | 11-4341-1 | 1ST EXT CENTRIFUGE 5400 OIL |  | North | OK | NR | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  | 8 | 12 | 5 | [6 empty] | Yes
MEM-PRO-011-XTR-2EX-4350 | MP1-5000 DESLUDGER DISCH PUMP | P1 Curd | 11-4350-0 | 5000 DESLUDGER DISCH PUMP |  | North | OK | OK | NR | OK | OK | OK | NR | NR | OK | NR | ok | OK | ok | ok | ok | NR | NR | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  | 6 | 12 | 5 | [6 empty] | Yes
MEM-PRO-011-XTR-1EX-4351 | MP1-P5400 1ST EXTRACT DISCH PUMP | P1 Curd | 11-4351-0 | P5400 1ST EXT DISCH PUMP N |  | North | OK | NR | OK | OK | OK | OK | NR | NR | OK | OK | ok | 2 | 2 | ok | ok | NR | ok | ok | ok | 2 | 3 | NR |  |  | 3 | Pump still has some vibration but lower overall... Not clear if work has been done or not?? | Pump still has some vibration but lower overall... Not clear if work has been done or not?? | 7269606 | #VALUE! | 2021-12-16 |  |  | 4 | 16 | 5 | [6 empty] | Yes
MEM-PRO-011-XTR-1EX-4352 | MP1-P5400 DESLUDGER DISCH SOLIDS PUMP | P1 Curd | 11-4352-0 | 5400 DESLUDGER DISCH PUMP S |  | North | NR | NR | OK | OK | 4 | 4 | NR | NR | 2 | 3 | 2 | 2 | 2 | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  | Pump data is showing signs of impacting and rpm harmonics which indicate issues in the pump. The feet bolts on the pump for this unit are loose and the pump loose to the base. It is recommended to replace pump, install new bolts with hardened washers and realign unit as soon as practical. Ensure coupling does not have excessive wear and gear drive is not defective. Rated as a CLASS III defect. | done |  | 2021-12-16 |  |  | 4 | 33 | 5 |  | drain sample with online filtering and oil coolier |  |  |  |  | Yes
MEM-PRO-011-XTR-2EX-4353 | MP1-P5000 DESLUDGER DISCH SOLIDS PUMP | P1 Curd | 11-4353-0 | P5000 DESLUDGER SOLIDS PUMP |  | New North | [24 empty] | NR |  | This pump is likely a duplicate of 11-4350. CANNOT LOCATE THIS PUMP! |  |  | 2021-09-30 |  |  | 8 | 16 | 5 | bar: NR to NR
MEM-PRO-011-WSH-CWH-4375 | MP1-#2 WASHING CENTRIFUGE | P1 Curd | 11-4375-0 | C30 #2 WASHING CENTRIFUGE |  | North | OK | OK | NR | OK | OK | OK | NR | NR | OK | 3 | 2 | 3 | 3 | 3 | 3 | 3 | ok | ok | NR | ok | ok | NR |  |  | 3 | Motor has increased axial vibration. Check sheaves and belts and ensure no face run-out or excessive misalignment during next avaialbe time. | looking better this month. | 7231149 | MCA | 2021-12-16 | mca needed |  | 8 | 8 | #N/A
MEM-PRO-011-WSH-CWH-4380 | MP1-#1 WASHING CENTRIFUGE | P1 Curd | 11-4380-0 | C30 #1 WASHING CENTRIFUGE |  | North | OK | 3 | NR | 3 | NR | OK | NR | NR | 3 | 3 | 2 | 3 | 3 | ok | 3 | 3 | 3 | 1 | 2 | 3 | 3 | NR |  |  | 3 | This motor also has increased axial vibration. Check sheaves and belts and ensure no face run-out or excessive misalignment during next avaialbe time. | about the same | 7267339 | #VALUE! | 2021-12-16 | Bowl and spindle replacemnt 7/7/20 | MCA needed | 8 | 24 | 5 | [6 empty] | Yes
MEM-PRO-011-WSH-WRE-4435 | MP1-CENTRIFUGE FEED PUMP | P1 Curd | 11-4435-0 | MP1-CENTRIFUGE FEED PUMP |  | North | OK | OK | NR | OK | OK | NR | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  | 6 | 4 | 5 | [6 empty] | Yes
MEM-PRO-011-CON-1SC-4495 | MP1-#2 CONCENTRATOR | P1 Curd | 11-4495-0 | CONCENTRATOR #2 |  | North | OK | NR | 4 | 4 | OK | OK | NR | NR | OK | 3 | 3 | 2 | 2 | 3 | 3 | 3 | 3 | 2 | ok | ok | ok | NR |  |  | OK |  | Centrifuge bearing data is still showing fit looseness is still present. Peakvue data also still indicates non-synchronous vibration with a fundamental of 7.97 orders of the DE bearing indicating a bearing issue in the DE bearing. Peakvue is also showing an increase in amplitude. Rated as a CLASS III defect. |  |  | 2021-12-16 |  |  | 12 | 4 | 5 | [6 empty] | Yes
MEM-PRO-011-CON-1SC-4495 | MP1-#2 CONCENTRATOR | P1 Curd | 11-4495-1 | CONCENTRATOR OIL PUMP #2) |  | North | OK | NR | OK | OK | OK |  | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  | 12 | 25 | 5 |  | drain sample with online filtering and oil coolier |  |  |  |  | Yes
MEM-PRO-011-CON-1SC-4500 | MP1-#1 CONCENTRATOR | P1 Curd | 11-4500-0 | CONCENTRATOR #1 |  | North | OK | NR | 2 | 2 | 3 | 3 | NR | NR | 4 | 3 | 3 | 3 | 3 | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  | Centrifuge vibration has increased this survey. Vibration is mainly at 1 x rpm and is over 1 ips at CIH. Unit needs to be cleaned out at earliest opportunity. Rated as a CLASS III defect. | done |  | 2021-12-16 | Running reduced curd flake rate due to #1 concentrator backdrive bad bearing. Took area down to build curd inventory from 0500-0915. |  | 12 | 4 | 5 |  | drain sample with online filtering and oil coolier |  |  |  |  | Yes
MEM-PRO-011-CON-1SC-4500 | MP1-#1 CONCENTRATOR | P1 Curd | 11-4500-1 | CONCENTRATOR OIL PUMP #1 |  | North | OK | NR | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  | done |  | 2021-12-16 |  |  | 12 | 25 | 5 |  | drain sample with online filtering and oil coolier
MEM-PRO-011-CON-1SC-4555 | MP1-CENTRIFUGE DESLUDGER GRINDER | P1 Curd | 11-4555-0 | REITZ CENTRIFUGE GRINDER |  | North | OK | OK | NR | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16
MEM-PRO-011-CON-1SC-4557 | MP1-IKA WORKS DISPAX GRINDER | P1 Curd | 11-4557-0 | CURD POT WET GRINDER |  | North | OK | OK | NR | OK | OK | OK | NR | NR | OK | NR | ok | 3 | 3 | 2 | 1 | 1 | 1 | NR | 1 | NR | NR | NR |  |  | NR |  | Grinder data show heavy impacting within the grinder unit. Spectral data shows extremely high noise floor indicating severe defect within the unit. Replace unit ASAP. Rated as a CLASS IV defect. | 7235300 | #VALUE! | 2021-10-12 | bad repair-possibe pipe strain.
MEM-PRO-011-CHL-CCS-4615 | MP1-#2 CHILL TANK DISCHARGE PUMP | P1 Curd | 11-4615-0 | #2 CHILL TANK DISCHARGE PUMP |  | North | NR | OK | OK | OK | NR | NR | NR | NR | OK | NR | NR | NR | ok | NR | ok | NR | OK | NR | NR | ok | ok | NR |  |  | NR |  |  |  |  | 2021-12-16 |  |  | 3
MEM-PRO-011-IDN-IDF-4695 | MP1-NEUTRAL TANK PH RECIRC. PUMP | P1 Curd | 11-4695-0 | NEUTRAL TANK PH RECIRC PUMP |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | NR | ok | OK | ok | NR | ok | NR | OK | OK | NR | ok | ok | NR |  |  | OK |  |  |  |  | 2021-11-09 |  |  | 5
MEM-PRO-011-BGY-FCS-4845 | MP1-N BOGEY VACUUMIZER DISCH PUMP | P1 Curd | 11-4845-0 | N BOGEY VACUUMIZER DIS PUMP |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | NR | 2 | 2 | 3 | NR | 3 | 3 | 3 | 1 | 1 | 1 | NR | NR |  |  | OK | Looks good since TAR repairs! | Motor vibration has increased significantly since replacing the pump. Alignment is good, but data shows some type of looseness in the motor. This may be loose coupling or bad motor fits. Inspect/replace motor/coupling ASAP. Rated as a CLASS IV defect. | 7261049 | #VALUE! | 2021-11-09 |  |  | 8 | 17 | #N/A | [6 empty] | Yes
MEM-PRO-011-BGY-FCS-4880 | MP1-N BOGEY CONDENSER DISCH PUMP | P1 Curd | 11-4880-0 | N BOGEY CONDENSER DISCH PUMP |  | North | NR | NR | NR | OK | 3 | 3 | NR | NR | 4 | NR | ok | OK | ok | NR | ok | ok | ok | ok | NR | ok | NR | NR |  |  | OK |  |  |  |  | 2021-11-09 |  |  | 4 | 16 | 5
MEM-PRO-011-BGY-FCS-4890 | BOGEY VACUUM PUMP | P1 Curd | 11-4890-0 | BOGEY VACUUM PUMP |  | North | OK | OK | OK | OK | OK | 3 | NR | NR | 2 | 4 | 3 | OK | NR | NR | ok | NR | ok | ok | NR | ok | NR | NR |  |  | 4 | Quite a bit of cavitation coming from the pump causing high acceleration amplitudes. | Pump flow issues | done |  | 2021-11-09 |  |  | 8 | 34 | 5 |  | drain sample with online filtering and oil coolier
MEM-PRO-011-CIP-SAC-5007 | MP1-CIP SUPPLY PUMP | P1 Curd | 11-5007-0 | MP1-CIP SUPPLY PUMP |  | New North | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | repair | Repair | Repair | repair | NR | NR |  |  | NR |  | need wireless |  |  | #N/A |  |  | 4 | 16 | 5
MEM-PRO-011-WEI-WIS-6430 | MP1-300T P1 FEED TRANSFER BLOWER | 300 Ton | 11-6430-0 | 300T P1 FEED TRANSFER BLOWER |  | North | OK | OK | OK | NR | OK | OK | NR | NR | OK | NR | NR | OK | NR | NR | NR | NR | NR | ok | ok | ok | NR | NR |  |  | NR |  |  |  |  | 2021-11-08 |  |  | 4 | 16 | 5
MEM-PRO-011-PKG-BLD-6640 | MP1B-PRODUCT COLLECTOR EXHAUST FAN | P3 Dryer | 11-6640-0 | PRODUCT COLLECTOR EXH FAN |  | North | NR | OK | NR | OK | NR | NR | OK | NR | OK | NR | ok | OK | ok | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 16 | 49
MEM-PRO-011-PKG-BLD-6650 | MP1B-BLENDER - RIBBON | P3 Dryer | 11-6650-0 | MP1B-BLENDER - RIBBON |  | North | OK | OK | OK | OK | NR | NR | OK | NR | 3 | 3 | 3 | 2 | 2 | 1 | 2 | 2 | 2 | ok | ok | ok | ok | NR |  |  | OK |  | Gearbox data shows high noise floor in spectral data. Waveform data shows heavy impacting which indicates some defects/wear are present internally in the gearbox. Gearbox will likely need to be replaced soon. Motor also has some increased 1 x rpm vibration. Coupling shot bead may be building up to one side creating an imbalance of the coupling. Rated as a CLASS III defect. |  |  | 2021-12-15 |  |  | 12
MEM-PRO-011-PKG-BLD-6657 | MP1B-BLENDER SEAL BLOWER | P1 Curd | 11-6657-0 | MP1B-BLENDER SEAL BLOWER |  | New North | [24 empty] | NR |  |  |  |  | #N/A |  |  | 2 | 16 | 5 | [6 empty] | Yes | bar: NR to NR
MEM-PRO-011-PKG-BLD-6660 | MP1B-DCE FILTER BLOWER | P3 Dryer | 11-6660-0 | BLENDER FILTER ASP BLOWER |  | North | OK | OK | NR | OK | NR | NR | OK | NR | OK | NR | 2 | 2 | 2 | NR | ok | NR | NR | ok | ok | ok | ok | NR |  |  | OK |  | Blower unit appears to have some internal issues. Blower likely needs replacing as soon as scheduling allows. Rated as a CLASS III defect. |  |  | 2021-12-15 |  |  | 4 | 18 | #N/A | [6 empty] | Yes
MEM-PRO-011-PKG-BLD-6815 | MP1B-BLENDER DISCHARGE BLOWER | P1 Curd | 11-6815-0 | P1B-BLENDER DISCHARGE BLOWER |  | New North | [24 empty] | NR |  |  |  |  | #N/A |  |  | 6 | 16 | 5 | bar: NR to NR
MEM-PRO-011-XTR-3EX-9319 | MP1 -3RD EXT FEED PUMP | P1 Curd | 11-9319-0 | 3RD EXTRACTION FEED PUMP |  | North | OK | OK | NR | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | NR | ok | NR | ok | ok | NR | NR |  |  | NR |  |  |  |  | 2021-11-09 |  |  |  | 19 | #N/A
MEM-PRO-011-XTR-1EX-9320 | MP1 1ST EXT EAST DCNTR PUMP | P1 Curd | 11-9320-0 | WEST 1ST DCNTR NX PUMP) |  | North | OK | NR | NR | 3 | OK | 3 | NR | NR | 2 | OK | ok | OK | ok | ok | ok | NR | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  |  | 16 | #N/A
MEM-PRO-011-XTR-1EX-9321 | MP1 1ST EXT EAST DCNTR SLDG PUMP | P1 Curd | 11-9321-0 | E 1ST EXT DCNTR SLDG NX PUMP |  | North | OK | NR | OK | OK | OK | OK | NR | NR | 2 | OK | ok | 2 | 3 | 3 | ok | ok | ok | ok | ok | NR | ok | NR |  |  | 3 | Motor has increased 1 x rpm vibration. Coupling needs to be checked as sceduling allows. | Gear drive still has a high acceleration amplitudes. Gear drive appears to be defective. Replace gear drive as scheduling allows. Rated as a CLASS II defect. | done |  | 2021-12-16 |  |  | 4 | 4 | 5 |  | drain sample with online filtering and oil coolier
MEM-PRO-011-XTR-3EX-9322 | MP1 3RD EXT DCNTR PUMP | P1 Curd | 11-9322-0 | 3RD EXTRACTION DCNTR NX PUMP |  | North | OK | NR | OK | OK | OK | OK | NR | NR | OK | 3 | 3 | OK | ok | ok | ok | NR | ok | ok | ok | ok | ok | NR |  |  | OK |  | motor alsignemnt and pump loose | done |  | 2021-11-09 |  |  |  | 24 | 5
MEM-PRO-013-WEI-WIS-0014 | MP3B-LIME BIN SCREW CONVEYOR | P3 Curd B | 13-0014 | MP3B-LIME BIN SCREW CONVEYOR |  | New North | [24 empty] | OK |  |  |  |  | 2021-12-15 |  |  | 4 | 24 | 5 | bar: NR to NR
MEM-PRO-013-WEI-WIS-0030 | MP3B-WET-IN PUMP | P3 Curd A | 13-0030 | MP3B-WET-IN PUMP |  | North | OK | OK | OK | NR | NR | OK | NR | NR | OK | 3 | 3 | 3 | 3 | ok | ok | ok | ok | ok | 3 | 3 | 3 | NR |  |  | 3 | Pump needs to be anchored down during next TAR. | Pump needs to be anchored down during next TAR. Motor Failed inDec on Sat | 7245813 |  | 2021-12-15 |  |  | 4 | 6 | 38
MEM-PRO-013-XTR-1EX-0043 | MP3B-1ST EXTRACTION TANK DISCH PUMP | P3 Curd A | 13-0043 | 1ST EXT TANK DISCH PUMP |  | North | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 12 | 8 | 5 |  |  | yes | No motor picture
MEM-PRO-013-WSH-WRE-0072 | MP3B-W RESLURRY POT PUMP | P3 Curd A | 13-0072 | W CON FEED RESLURRY POT PUMP |  | North | OK | OK | 2 | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 6 | 16 | 5 |  |  | yes | No motor picture
MEM-PRO-013-CON-CON-0075 | MP3B-#5 CONCENTRATOR PRODUCT POT | P3 Curd A | 13-0075 | #5 CONCENTRATION CENTRIFUGE |  | North | OK | OK | 4 | OK | OK | OK | NR | NR | OK | 3 | 1 | 3 | 3 | 3 | NR | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  | High acceleration remains in the motor especially at the drive end. This appears to be electrically related. Online and offline PdMA testing may help clarify this issue. Centrifuge also has high inboard vertical vibration. High 1 x rpm peak indicates imbalance of the centrifuge. Rated as a CLASS II defect. | done |  | 2021-12-15 | 7/28/20 backdrive, jackshaft, and sungear replac |  |  | 16 | 5 |  |  | yes | No motor picture |  |  | Yes
MEM-PRO-013-CON-CON-0075 | MP3B-#5 CONCENTRATION CENTRIFUGE | P3 Curd A | 13-0075-1 | #5 CON CENTRIFUGE OIL PUMP |  | North | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | ok | OK | ok | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  | done |  | 2021-12-15 |  |  |  | 16 | 5 |  |  | yes | No motor picture |  |  | Yes
MEM-PRO-013-PCP-PHA-0082 | MP3B-CLARIFIED TANK PUMP | P3 Curd A | 13-0082 | CLARIFIED TANK DISCH PUMP |  | North | OK | OK | OK | NR | NR | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 6 | 16 | #N/A | [6 empty] | Yes
MEM-PRO-013-PCP-PCT-0084 | MP3B-PRECIPITATION TANK DISCH PUMP | P3 Curd A | 13-0084 | C30 PRECIP FEED TANK PUMP |  | North | OK | OK | OK | NR | NR | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | 3 | 3 | 3 | NR |  |  | 3 | Motor should be changed out during next TAR. Data indincates defects in motor bearings. | Motor data is starting to show signs of motor bearing defects. Motor should be replaced during the next opportunity. Rated as a CLASS II defect. | 7267372 | #VALUE! | 2021-12-15 |  |  | 6 | 8 | 5
MEM-PRO-013-WSH-CWH-0085 | MP3B-#1 WASHING CENTRIFUGE | P3 Curd A | 13-0085 | C30 #1 WASHING CENTRIFUGE |  | North | OK | OK | 4 | OK | OK | OK | NR | NR | 1 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | ok | ok | ok | ok | NR |  |  | OK |  | Overall vibration of the centrifuge inboard bearing remains high at 1.38 ips pk! Bowl is still showing some balance. Motor data is also showing some bearing defect frequencies present in the acceleration spectra of the motor inboard bearing. For now, Unit needs cleaned out soon. If 1 x rpm remains after clean out then bowl unit may need replacing Rated as a CLASS III defect. |  |  | 2021-12-15 |  |  |  | 8 | 5
MEM-PRO-013-WSH-CWH-0086 | MP3B-#2 WASHING CENTRIFUGE | P3 Curd A | 13-0086 | C30 #2 WASHING CENTRIFUGE |  | North | OK | OK | 4 | OK | 1 | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | 3 | ok | ok | ok | ok | ok | NR |  |  | OK |  | imbalance |  |  | 2021-12-15 |  |  |  | 8 | 5 |  |  | yes | No motor picture
MEM-PRO-013-WSH-CWH-0087 | MP3B-#3 WASHING CENTRIFUGE | P3 Curd A | 13-0087 | C30 #3 WASHING CENTRIFUGE |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | 3 | 2 | 2 | 2 | 2 | ok | ok | ok | NR |  |  | OK |  | Motor has bearings defects according to vibration data and needs to be changed out as soon as practical. CHANGE MOTOR SOON and ensure sheaves are properly aligned. Rated as a CLASS III defect. |  |  | 2021-12-15
MEM-PRO-013-CON-CON-0096 | MP3B-#3 CONCENTRATION CENTRIFUGE-P500 | P3 Curd A | 13-0096 | #3 CONCENTRATION CENTRIFUGE |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | 3 | 3 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | NR |  |  | 1 | Back drive bearings VIBRATION HAS INCREASED and data is showing strong beairng defects. NEEDS ATTTETION ASAP!! Also drive motor still shows rotor bar issues. Not sure if online PDMA tsting has been done yet… | Back drive bearings VIBRATION HAS INCREASED and data is showing strong beairng defects. NEEDS ATTTETION ASAP!! Also drive motor still shows rotor bar issues. Not sure if online PDMA tsting has been done yet… | 7274552 | MCA | 2021-12-15 |  |  |  | 8 | 5 | [6 empty] | Yes
MEM-PRO-013-CON-CON-0096 | MP3B-#3 CONCENTRATION CENTRIFUGE-P500 | P3 Curd A | 13-0096-1 | #3 CON CENTRIFUGE OIL PUMP |  | North | NR | OK | OK | 3 | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | OK | OK | OK | OK | OK | OK | ok | NR |  |  | OK |  | MIV remains near 1 ips-pk. Motor has high 1 x motor rpm vibration with some harmonics and electrical related vibrations (rotor bar pass) which may indicate rotor issue. Data also shows a high sub-harmonic vibration which is very concerning this survey. Online and offline PdMA testing may clarify this issue; however, we recommend that motor be swapped out at earliest opportunity. Rated as a CLASS III defect. |  |  | 2021-12-15 |  |  |  | 16 | 5 |  |  | yes | No motor picture
MEM-PRO-013-CON-CON-0097 | MP3B-#2 CONCENTRATION CENTRIFUGE | P3 Curd A | 13-0097 | #2 CONCENTRAION CENTRIFUGE |  | North | 2 | OK | 4 | OK | OK | OK | NR | NR | 3 | 3 | 3 | OK | ok | 2 | 3 | 2 | 2 | 2 | ok | ok | ok | NR |  |  | 2 | Main Drive Motor is starting to show some signs that defects are present in motor bearings. Motor should be scheduled to replace during next TAR. | Centrifuge has some higher-than-normal vertical vibration. This may be structural but also is likely due to some imbalance of the centrifuge. Replace secondary bearings, clean out centrifuge, ensure sheaves/couplings are in good shape, and ensure all fasteners are tight. Rated as a CLASS III defect. | done |  | 2021-12-15 | #N/A |  |  | 16 | 5 |  |  | yes | No motor picture
MEM-PRO-013-CON-CON-0097 | MP3B-#2 CONCENTRATION CENTRIFUGE | P3 Curd A | 13-0097-1 | #2 CON CENTRIFUGE OIL PUMP |  | North | NR | OK | OK | OK | NR | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 16 | 37
MEM-PRO-013-CON-CON-0099 | MP3B-#4 CONCENTRATION CENTRIFUGE | P3 Curd A | 13-0099 | #4 CONCENTRATION CENTRIFUGE |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 3 | 3 | ok | NR |  |  | 4 | Motor has some electrical vibration. 120 Hz. sidebands are good indication of possilbe issue. PDMA may help..online and offline tests shuld be performed as scheduling allows. | motor vibration has decreased. | done |  | 2021-12-15 |  |  |  | 16 | 5 |  |  | yes | No motor picture
MEM-PRO-013-CON-CON-0099 | MP3B-#4 CONCENTRATION CENTRIFUGE | P3 Curd A | 13-0099-1 | #4 CON CENTRIFUGE OIL PUMP |  | North | NR | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 16 | 5 |  |  | yes | No motor picture
MEM-PRO-013-WSH-WRE-0120 | MP3B-E RESLURRY POT DISCH PUMP | P3 Curd A | 13-0120 | E RESLURRY POT DISCH PUMP |  | North | OK | OK | OK | OK | 3 | 4 | NR | NR | 4 | 3 | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  | replace pump | done |  | 2021-12-15 |  |  | 4
MEM-PRO-013-CON-CRE-0137 | MP3B-#1/#2 CONC PRODUCT POT GRINDER | P3 Curd A | 13-0137 | N REITZ PRODUCT POT GRINDER |  | North | OK | OK | OK | OK | OK | OK | NR | NR | NR | OK | ok | OK | ok | NR | NR | NR | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15
MEM-PRO-013-WSH-CWH-0145 | MP3B-#5 WASHING CENTRIFUGE | P3 Curd A | 13-0145 | C30 #5 WASHING CENTRIFUGE |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | 2 | 1 | 1 | NR |  |  | 1 | NEED TO CONFIRM IF MOTOR WAS CHANGED RECENTLY!! Motor appears to have some higher than normal electrical vibrations. May be a connection issue. PDMA online and offline should be perfromed soon. | Not much change. Motor bearings are BAD. Replace motor soon. | 7267373 | #VALUE! | 2021-12-23
MEM-PRO-013-CON-CRE-0165 | MP3B-#3/4 CONC PRODUCT POT GRINDER | P3 Curd A | 13-0165 | S REITZ PRODUCT POT GRINDER |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | 1 | ok | OK | ok | NR | NR | NR | ok | ok | ok | ok | ok | NR |  |  | OK |  | bearing gone | done |  | 2021-12-15
MEM-PRO-013-WSH-CWH-0278 | MP3B-#4 WASHING CENTRIFUGE | P3 Curd A | 13-0278 | C30 #4 WASHING CENTRIFUGE |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | NR |  |  | 4 | Bowl speed vibration has decreased. Motor data shows some electrical vibrations. Will monitor closely. | high 1 x bowl rpm present indicating imbalance of the bowl. | flush |  | 2021-12-15
MEM-PRO-013-CON-CON-0279 | MP3B-#1 CONCENTRATION CENTRIFUGE | P3 Curd A | 13-0279 | #1 CONCENTRATION CENTRIFUGE |  | North | OK | OK | NR | OK | 1 | OK | NR | NR | 2 | 2 | 2 | 3 | 3 | ok | ok | 3 | 2 | 1 | 1 | ok | 2 | NR |  |  | 3 |  | Motor has high vertical vibration likely due to motor not having a good mount for drive end motor feet. Also back end small pillow block bearings look better this survey. Work has likely been performed recently. | 7274553 |  | 2021-12-15
MEM-PRO-013-CON-CON-0279 | MP3B-#1 CONCENTRATION CENTRIFUGE | P3 Curd A | 13-0279-1 | #1 CON CENTRIFUGE OIL PUMP |  | North | NR | OK | NR | 3 | NR | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15
MEM-PRO-013-XTR-3EX-0291 | MP3B-S 3RD EXTRACTION DISCH PUMP | P3 Curd A | 13-0291 | S 5000 3RD EXT DISCH PUMP |  | North | OK | OK | OK | NR | OK | OK | NR | NR | NR | OK | ok | OK | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | NR |  |  | 2 | No change this month. Motor still shows issues. | Motor still has bearing defects. Replace motor during next TAR. | 7274554 | #VALUE! | 2021-12-21 |  |  |  | 16 | #N/A
MEM-PRO-013-FED-SLT-0295 | MP3B-S DESLUDGER SOLIDS CONVEYOR | P3 Alget Dryer | 13-0295 | S DESLUDGER SOLIDS CONVEYOR |  | New North | [24 empty] | NR |  |  |  |  | 2021-08-25 |  |  | 6 | 27 | #N/A |  | drain sample with online filtering and oil coolier | bar: NR to NR
MEM-PRO-013-XTR-3EX-0299 | MP3B-S 3RD EXTRACTION CENTRIFUGE | P3 Curd A | 13-0299 | S 5400 3RD EXT CENTRIFUGE |  | North | OK | OK | 4 | OK | 1 | OK | NR | NR | OK | OK | ok | OK | 3 | 2 | ok | 3 | 3 | 3 | 3 | 3 | 1 | NR |  |  | 3 | Motor has a high 1 x rpm vibration. Ensure fastneners are tight, check motor sheave for face run-out and alignment. Ensure belts are in good shape. Centrifuge bearings look good for now. | P3 13-0299 bad bearings(cage). Change out as soon as possible Class IV. Bearing cage peaks are not present anymore..not sure what is going on right now. Motor also shows some rotor bar vibrations. Will continue to monitor CLOSELY. | 7274555 | #VALUE! | 2021-12-15 |  |  |  | 16 | #N/A
MEM-PRO-013-XTR-3EX-0299 | MP3B-S 3RD EXTRACTION CENTRIFUGE | P3 Curd A | 13-0299-1 | S 5400 3RD EXT CENT OIL P |  | North | OK | NR | OK | OK | NR | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | OK | ok | NR |  |  | OK |  |  |  |  | 2021-12-15
MEM-PRO-013-XTR-3EX-0300 | MP3B-N 3RD EXTRACTION CENTRIFUGE | P3 Curd A | 13-0300 | N 5000 3RD EXT CENTRIFUGE |  | North | OK | OK | OK | 3 | OK | OK | NR | NR | NR | OK | ok | OK | ok | ok | 3 | ok | 2 | ok | ok | ok | ok | NR |  |  | 3 | Centrifuge has increased 1 x rpm vibration. This is likely imbalance of the centrifuge assembly. |  |  |  | 2021-12-15 |  |  |  | 33 | #N/A
MEM-PRO-013-XTR-3EX-0300 | MP3B-N 3RD EXTRACTION CENTRIFUGE | P3 Curd A | 13-0300-1 | N 5000 3RD EXT CENT OIL PUMP |  | North | NR | OK | OK | OK | OK | OK | NR | NR | NR | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | Ok |  |  |  |  | 2021-12-15 |  |  |  | 4 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-XTR-3EX-0301 | MP3B-N DESLUDGER EXTRACT DISCH PUMP | P3 Curd A | 13-0301 | N 5400 DESL 3RD EXT DIS PUMP |  | North | OK | OK | OK | OK | NR | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 33 | #N/A
MEM-PRO-013-CON-CRE-0458 | MP3B-#5 CONC PRODUCT POT PUMP | P3 Curd A | 13-0458 | #5 CONC PRODUCT POT DIS PUMP |  | North | OK | OK | OK | NR | OK | OK | NR | NR | NR | OK | ok | OK | ok | NR | NR | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 4 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-CON-CRE-0580 | MP3B-#5 CONC CENT PROD POT AGITATOR | P3 Curd A | 13-0580 | 5 CON CENT PROD POT AGITATOR |  | North | OK | OK | OK | NR | NR | OK | NR | NR | NR | OK | ok | OK | ok | NR | NR | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 33 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-FED-SLT-0594 | MP3B-SCREW CONV FROM 3RD EXT SOLIDS | P3 Alget Dryer | 13-0594 | SCREW CONV FROM DESLUD SOLID |  | New North | [24 empty] | NR |  |  |  |  | 2021-08-25 |  |  | 6 | 4 | #N/A |  | drain sample with online filtering and oil coolier | bar: NR to NR
MEM-PRO-013-CON-CON-0610 | MP3B-#6 CONCENTRATION CENTRIFUGE | P3 Curd A | 13-0610 | #6 CONCENTRATION CENTRIFUGE |  | North | OK | OK | OK | OK | 2 | OK | NR | NR | OK | NR | NR | 2 | OK | ok | 3 | 2 | 2 | 2 | 2 | 2 | 2 | NR |  |  | 1 | Back end of the unit has major issues. Vibration is well over 1 ips and a huge increase from last month! The small bearings are showing signs of loosenes/wear especially the outboard bearing (closest to brake). There is also high vibration in the back end brake assembly. Ensure all couplings, brake assembly,and bearings are in good order and not loose. INSPECT ASAP! | high 1 x rpm vibration at centrifuge verticals especially at the back end small pillow block bearings. Inspect back end couplings and ensure no build up in centrifuge. | 7269617 | #VALUE! | 2021-12-15 |  |  |  | 33 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-CON-CON-0610 | MP3B-#6 CONCENTRATION CENTRIFUGE | P3 Curd A | 13-0610-1 | #6 CON CENTRIFUGE OIL PUMP |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 4 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-XTR-2EX-0620 | MP3B-EAST 2ND EXTRACTION CENTRIFUGE | P3 Curd A | 13-0620 | E 5400 2ND EXT CENTRIFUGE |  | North | OK | OK | 2 | NR | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | NR | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 33 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-XTR-2EX-0620 | MP3B-EAST 2ND EXTRACTION CENTRIFUGE | P3 Curd A | 13-0620-1 | E 5400 2ND EXT CENT OIL P |  | North | OK | OK | OK | NR | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 4 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-CON-CRE-0628 | MP3B-#6 CONC PRODUCT POT AGITATOR | P3 Curd A | 13-0628 | #6 CONC PRODUCT POT AGITATOR |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | OK | NR | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 33 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-CON-CRE-0630 | MP3B-#6 CONC PRODUCT POT PUMP | P3 Curd A | 13-0630 | #6 CONC PRODUCT POT PUMP |  | North | OK | OK | OK | NR | OK | OK | NR | NR | OK | OK | NR | OK | ok | ok | ok | ok | ok | ok | ok | ok | 2 | NR |  |  | OK | Pump looks better this month. | Pump is showing some signs of wear. A heavy impact can be seen in Peakvue and acceleration waveform data. This is a good indication of internal pump issues. | 7274556 |  | 2021-12-15 |  |  |  | 4 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-PKG-PAK-2181 | MP3B - BLENDER | P3 Dryer | 13-2181 | MP3B-BLENDER |  | North | OK | OK | NR | 4 | 4 | NR | 3 | NR | OK | NR | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | ok | ok | NR | NR |  |  | 4 | Motor data still shows some electrically related vibrations in the motor. Online PdMA testing may help determine severity. We are watching this issue closely. As far as the gearbox goes, data still shows a high noise floor while amplitudes remain steady. We still suspect a possible gear issue. | Motor data still shows some electrically related vibrations in the motor. Online PdMA testing may help determine severity. We are watching this issue closely. Motor also has a 1 x rpm axial vibration that may be coupling related. As far as the gearbox goes, data still shows a high noise floor while amplitudes remain steady. We still suspect a possible gear issue. |  |  | 2021-11-10 |  |  | 8 | 16 | #N/A
MEM-PRO-013-PKG-PAK-2184 | MP3B - BLENDER ASP FILTER EXH FAN | P3 Dryer | 13-2184 | BLENDER ASP FILTER EXH FAN |  | North | OK | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | ok | NR | NR | NR | NR | NR | NR | NR |  |  | NR |  | changed motor on 9/11/21 |  |  | 2021-06-21 |  |  | 1 | 8 | #N/A
MEM-PRO-013-PKG-PAK-2188 | MP3B-BLENDER DISCH BLOWER | P3 Dryer | 13-2188 | MP3B-BLENDER DISCH BLOWER |  | North | [24 empty] | NR |  | Wireless Recommended X 3 |  |  | 2021-08-31 |  |  | 1 | 8 | #N/A | bar: NR to NR
MEM-PRO-013-PKG-PAK-2198 | MP3B- W PRODUCT SCREENER | P3 Dryer | 13-2198 | NIRO W AZO PRODUCT SCREENER |  | North | [24 empty] | OK |  |  |  |  | 2021-09-30 |  |  | 1 | 16 | #N/A | bar: NR to NR
MEM-PRO-013-PKG-PAK-2208 | MP3B-NIRO PK'ER SURGE BIN ASP FAN | P3 Dryer | 13-2208 | NIRO PK'ER SURGE BIN ASP FAN |  | North | [24 empty] | NR |  |  |  |  | 2021-09-14 |  |  | 1 | bar: NR to NR
MEM-PRO-013-PKG-PAK-2257 | MP3B-BB PRODUCT SCREENER | P3 Dryer | 13-2257 | AZO BB PRODUCT SCREENER |  | North | OK | OK | NR | OK | NR | NR | NR | NR | NR | NR | 2 | NR | NR | NR | NR | NR | ok | ok | NR | NR | NR | NR |  |  | NR |  | motor loosness |  |  | 2021-09-30 |  |  | 1 | 16 | #N/A
MEM-PRO-013-PKG-PAK-2262 | MP3B-BB REC EXHAUST FAN | P3 Dryer | 13-2262 | SEMI BULK BB REC EXHAUST FAN |  | North | OK | NR | NR | OK | NR | NR | NR | NR | NR | NR | 3 | NR | NR | NR | NR | NR | ok | NR | NR | NR | NR | NR |  |  | NR |  | Get Data in June |  |  | 2021-08-31 |  |  | 1 | 32 | #N/A
MEM-PRO-013-SPR-DRY-2431 | MP3B-INLET FAN | P3 Dryer | 13-2431 | MP3B-INLET FAN |  | North | OK | OK | NR | OK | OK | OK | OK | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 16 | 16 | #N/A
MEM-PRO-013-SPR-DRY-2448 | MP3B-COOLING RING FAN | P3 Dryer | 13-2448 | MP3B-COOLING RING FAN |  | North | OK | OK | OK | OK | OK | OK | OK | NR | OK | 3 | 3 | 3 | 3 | 3 | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  | Motor verticals are still showing high vertical vibration. Dominant vibration is at 1 x rpm of the fan or motor. It is difficult to determine which it is because the speeds are very close. For now, it is recommended to inspect the motor/base fasteners, sheaves for looseness, misalignment, and belts for proper tension and wear. Rated as a CLASS II defect. |  |  | 2021-12-15 |  |  | 8 | 12 | #N/A
MEM-PRO-013-SPR-AIS-2524 | MP3B-S BAGHOUSE CONE HEATER BLOWER | P3 Dryer | 13-2524 | S BAGHOUSE CONE HEAT BLOWER |  | North | OK | OK | NR | OK | OK | OK | OK | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 12 | #N/A
MEM-PRO-013-SPR-DRY-2531 | MP3B-N EXHAUST FAN | P3 Dryer | 13-2531 | MP3B-N EXHAUST FAN |  | North | OK | OK | NR | OK | OK | OK | OK | NR | OK | 3 | 3 | 3 | 3 | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | 4 | Motor and fan have had an increased 1 x rpm vibration. This may be speed related. Will monitor closely. | Overall vibration was much lower this month likely because fan was operating at a slightly lower speed. This fan is suspected to be operating near a resonant frequency that coincides with the 1 x rpm of the unit. The peakvue data is still showing some early outboard fan bearing defect frequencies. Efforts may need to be made to keep this fan from operating at the speed of 1450-1550 rpm to help keep amplitudes down. Rated as a CLASS II defect. |  |  | 2021-12-15 |  |  | 16 | 12 | #N/A
MEM-PRO-013-SPR-DRY-2535 | MP3B-S EXHAUST FAN | P3 Dryer | 13-2535 | MP3B-S EXHAUST FAN |  | North | OK | OK | NR | OK | OK | OK | OK | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 16 | 12 | #N/A
MEM-PRO-013-SPR-PRC-2545 | MP3B-PRODUCT MILL GRINDER | P3 Dryer | 13-2545 | MP3B-PRODUCT MILL GRINDER |  | North | OK | OK | NR | OK | 4 | OK | OK | NR | OK | OK | ok | OK | ok | NR | ok | OK | 3 | 3 | 3 | 3 | 3 | NR |  |  | 3 | Grinder still has grinder rpm harmonic vibration. Motor alSO has high acceleration liekly due TO THE FACT THAT THE MOTOR DOES NOT HAVE A ROLLER BEARING IN THE DE. NEEDS A NU SERIES BEARING FOR RADIAL LOAD. Check grinder for fit looseness or other loose components. | motor replaced on 12/20/21 |  | #VALUE! | 2021-12-15 |  |  | 8 | 12 | #N/A
MEM-PRO-013-SPR-DRY-2558 | MP3B-PRODUCT SURGE BIN EXHAUST FAN | P3 Dryer | 13-2558 | PRODUCT SURGE BIN EXH FAN |  | North | OK | OK | NR | OK | OK | NR | OK | NR | OK | OK | 2 | 2 | 2 | 2 | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  | Spectral data of the fan bearings shows several rpm harmonics present which is indicative of mechanical looseness. Bearings and shaft need to be inspected ASAP. Shaft may have excessive wear. Rated as a CLASS III defect. |  |  | 2021-12-15 |  |  | 8 | 16 | #N/A
MEM-PRO-013-BLD-AHU-2680 | MP3B-N BAGHOUSE CONE HEATER BLOWER | P3 Dryer | 13-2680 | N BAGHOUSE CONE HEAT BLOWER |  | North | OK | OK | NR | OK | OK | OK | OK | NR | OK | OK | ok | OK | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | NR |  |  | 3 |  | Blower bearings need to be changed out as soon as practical. REPLACE BEARINGS DURING NEXT AVAILABILITY!!!! | 7240380 | #VALUE! | 2021-12-15 |  |  |  | 16 | #N/A
MEM-PRO-013-FED-FED-3026 | MP3B-FEED DRYER VENT FILTER EXHAUST FAN | P3 Alget Dryer | 13-3026 | FD VENT FILTER EXHAUST FAN |  | North | NR | OK | OK | OK | OK | OK | NR | NR | NR | NR | 3 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | NR | 3 | 2 | NR |  |  | 2 | Motor base is broken. Fasteners are missing!! Fan bearings are ok for now. MOTOR BASE Needs to be replaced as soon as practical!! | Motor base is broken. Fasteners are missing!! Fan bearings are ok for now. MOTOR BASE Needs to be replaced as soon as practical!! | 7271706 | #VALUE! | 2021-12-16 |  |  |  | 16 | #N/A
MEM-PRO-013-FED-FED-3036 | MP3B-FD DISCHARGE TO FEED LOADOUT RFV | P3 Alget Dryer | 13-3036 | FD DISCH TO FEED LOADOUT 036 |  | New North | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | NR | OK | NR | NR | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-16 |  |  | 4 | 16 | #N/A
MEM-PRO-013-FED-FED-3045 | MP3B-FEED LOADOUT BLOWER | P3 Alget Dryer | 13-3045 | FEED LOADOUT BLOWER |  | North | NR | OK | OK | OK | OK | OK | NR | NR | NR | OK | ok | OK | ok | NR | 3 | 3 | 3 | NR | NR | 3 | 3 | NR |  |  | 3 | Motor still has some vertical vibration. Likely due to structural issue. | Motor still has some vertical vibration. Likely due to structural issue. | 7251038 | #VALUE! | 2021-12-16 |  |  | 6 | 16 | 5 | [6 empty] | Yes
MEM-PRO-013-FED-SLT-3257 | MP3B-FEED DRYER MIXING CONVEYOR | P3 Alget Dryer | 13-3257 | FEED DRYER MIXING CONVEYOR |  | New North | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | NR | NR | ok | NR | NR |  |  | NR |  |  |  |  | 2021-11-08 |  |  | 6 | 4 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-FED-FED-3399 | MP3B-ALJET DRYER INLET FAN | P3 Alget Dryer | 13-3399 | MP3B-ALJET DRYER INLET FAN |  | North | NR | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | 3 | ok | ok | ok | NR | ok | ok | NR |  |  | OK |  | Outboard fan bearing data is showing signs of either a lubrication issue or bearing wear. For now, it is recommended to perform a visual inspection of the fan bearing ensuring grease is clean and of adequate amount as soon as scheduling allows. Rated as a CLASS II defect. |  |  | 2021-12-16 |  |  | 16 | 25 | #N/A |  | Gearbox
MEM-PRO-013-FED-FED-3407 | MP3B-FEED DRYER INFEED SCREW CONVEYOR | P3 Alget Dryer | 13-3407 | FD INFEED SCREW CONVEYOR |  | New North | [24 empty] | NR |  |  |  |  | 2021-08-31 |  |  | 6 | 16 | #N/A | bar: NR to NR
MEM-PRO-013-FED-FED-3409 | MP3-FEED DRYER PRIM CYCL TRANS BLR | P3 Alget Dryer | 13-3409 | FD PRIM CYCL TRANS BLOWER |  | North | NR | OK | OK | OK | OK | OK | NR | NR | NR | OK | ok | OK | ok | NR | 3 | 3 | 3 | NR | NR | ok | ok | NR |  |  | OK |  | Equipment was down this survey however, the following likely still applies: Motor vertical vibration have increased. Data shows high 1 x rpm vibration which may be structurally related. Frame does not appear to be adequate for this size of motor and could be resonant or flexible. Ensure all fasteners are tight and sheaves are aligned properly. Base may need modifications.in the future. Rated as a CLASS II defect. | done |  | 2021-12-16 |  |  | 6 | 16 | #N/A
MEM-PRO-013-FED-FED-3418 | MP3B-FEED DRYER EXHAUST FAN | P3 Alget Dryer | 13-3418 | MP3B-FEED DRYER EXHAUST FAN |  | North | NR | OK | OK | 4 | OK | OK | NR | NR | NR | OK | ok | OK | 3 | ok | 3 | 3 | 3 | 3 | NR | ok | ok | NR |  |  | OK |  | Been looking good since TAR actions. |  |  | 2021-12-16 |  |  | 8 | 16 | #N/A
MEM-PRO-013-FED-FED-3419 | MP3B-FEED BAGHOUSE SCREW CONVEYOR | P3 Alget Dryer | 13-3419 | FEED BAGHOUSE SCREW CONVEYOR |  | New North | [24 empty] | NR |  |  |  |  | 2021-08-31 |  |  | 6 | 33 | #N/A |  | drain sample with online filtering and oil coolier | bar: NR to NR
MEM-PRO-013-FED-FED-3422 | MP3B-FEED DRYER SCREW CONVEYOR | P3 Alget Dryer | 13-3422 | FEED DRYER SCREW CONVEYOR |  | New North | [24 empty] | NR |  |  |  |  | 2021-08-31 |  |  | 6 | 4 | #N/A |  | drain sample with online filtering and oil coolier | bar: NR to NR
MEM-PRO-013-UTL-CSY-4704 | LIME SLURRY TANK AGITATOR | P3 Curd B | 13-4704 | LIME SLURRY TANK AGITATOR |  | New North | [24 empty] | OK |  |  |  |  | 2021-12-15 |  |  | 3 | 25 | #N/A |  | drain sample with online filtering and oil coolier | bar: NR to NR
MEM-PRO-013-UTL-CSY-4714 | LIME SLURRY PUMP | P3 Curd B | 13-4714 | LIME SLURRY PUMP |  | North | NR | NR | OK | OK | NR | OK | NR | NR | OK | OK | ok | OK | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | NR |  |  | 2 | This pump has had a decrease in 1 x rpm vibration. This pump appears to run at variable speeds. The pump isnt supported well and may be resonant. Pump needs to be anchored to the base properly as soon as scheduling allows. | Pump needs to be properly anchored. High 1 x and 2 x rpm vibration present in pump. Schedule for next TAR! | 7269643 | #VALUE! | 2021-12-15 |  |  |  | 4 | #N/A |  | drain sample with online filtering and oil coolier
MEM-PRO-013-CHL-CCS-6115 | MP3B-N #3/S #4 CHILL TANK DISCH PUMP | P3 Curd B | 13-6115 | CHILL TANK DISCH PUMP |  | North | OK | NR | OK | OK | OK | OK | OK | NR | OK | OK | 2 | OK | ok | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  | motor alignment and torque | done |  | 2021-12-15 |  |  | 8 | 16 | #N/A
MEM-PRO-013-IDN-IDF-6124 | MP3B-IDN FEED PUMP | P3 Curd B | 13-6124 | IDN TANK DISCHARGE FEED PUMP |  | North | OK | NR | 4 | OK | OK | OK | OK | NR | OK | 3 | 3 | 3 | 3 | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  | Motor data shows an increase acceleration. Motor bearings are likely defective. Replace as soon as scheduling allows. Rated as a CLASS II defect. | done |  | 2021-12-15 |  |  | 6 | 16 | #N/A
MEM-PRO-013-BGY-FCS-6243 | MP3B-700 VACUUMIZER CONDENSATE PUMP | P3 Curd B | 13-6243 | 700 VACUUMIZER COND PUMP |  | North | OK | NR | OK | OK | OK | NR | OK | NR | NR | NR | ok | OK | ok | NR | ok | ok | ok | ok | ok | NR | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 4 | 16 | #N/A
MEM-PRO-013-BGY-FCS-6244 | MP3B-700 VACUUMIZER VACUUM PUMP | P3 Curd B | 13-6244 | 700 VACUUMIZER VACUUM PUMP |  | North | OK | NR | OK | OK | OK | NR | OK | NR | NR | NR | ok | OK | ok | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 12 | 8 | 43
MEM-PRO-013-BGY-FCS-6251 | MP3B-700 VACUMMIZER DISCH PUMP | P3 Curd B | 13-6251 | 700 VACUUMIZER DISCH PUMP |  | North | OK | NR | OK | OK | OK | NR | OK | NR | OK | OK | ok | OK | ok | NR | ok | ok | ok | ok | ok | NR | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 8 | 16 | 43
MEM-PRO-013-BGY-FCS-6266 | MP3B-S 600 VACUMMIZER DISCHARGE PUMP | P3 Curd B | 13-6266 | S 600 VACUUMIZER DISCH PUMP |  | North | OK | NR | OK | OK | OK | OK | OK | NR | NR | NR | 3 | 3 | 2 | 2 | ok | ok | ok | ok | ok | NR | ok | NR |  |  | OK |  | Motor and pump are showing signs of bearing defects and motor also has 2 x rpm vibration. Motor, pump, and couplings should be replaced during TAR. Rated as a CLASS III defect |  |  | 2021-12-15 |  |  | 8 | 16 | 5
MEM-PRO-013-IDN-IDF-6286 | MP3B-NEUTRALIZATION TK DISCHARGE PUMP | P3 Curd B | 13-6286 | NEUTRALIZATION TK DISCH PUMP |  | North | OK | NR | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | ok | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 4 | 16 | 43 | [6 empty] | Yes
MEM-PRO-013-BGY-FCS-6293 | MP3B-N 600 VAC VACUUM PUMP (WEST) | P3 Curd B | 13-6293 | N 600 VAC VACUUM PUMP WEST |  | North | OK | NR | 4 | OK | 4 | 4 | OK | NR | 4 | NR | ok | OK | 2 | 2 | 2 | 2 | 2 | 2 | 2 | NR | ok | NR |  |  | 3 | Pump has cavitation and also base needs to be replaced and regrouted as time allows. | Need to confirm if work was done on this equipment during TAR. Current data from 10/13/21 shows the following: Grinder has high 1 x rpm vibration. Grinder assembly may still have some imbalance. Ensure sheaves are not worn, aligned properly with minimal face run-out on the sheave and ensure belts are not worn and properly tensioned. Ensure adjustable motor base is not defective and all fasteners are tight. Rated as a CLASS III defect. |  |  | 2021-12-15 |  |  | 12 | 16 | 43
MEM-PRO-013-IDN-HYS-6326 | MP3B-W BATCH TANK DISCHARGE PUMP | P3 Curd B | 13-6326 | W BATCH TANK DISCHARGE PUMP |  | North | NR | NR | NR | NR | NR | OK | NR | NR | NR | OK | ok | 2 | OK | NR | ok | NR | ok | NR | ok | NR | ok | NR |  |  | OK |  | Motor and pump 2 x rpm vibration has increased this survey, especially in the vertical direction. Motor spectra also shows defects are present in the bearings while pump data is showing signs of internal wear. Check all fasteners and couplings/alignment immediately and schedule the motor, pump, and impeller to be replaced as soon as scheduling allows. Rated as a CLASS III defect. |  |  | 2021-12-15 |  |  | 6 | 16 | 5 | [6 empty] | Yes
MEM-PRO-013-IDN-HYS-6327 | MP3B-E BATCH TANK DISCHARGE PUMP | P3 Curd B | 13-6327 | E BATCH TANK DISCHARGE PUMP |  | North | OK | NR | 4 | 4 | 4 | 1 | OK | NR | 3 | OK | ok | OK | ok | NR | NR | ok | ok | ok | ok | NR | NR | NR |  |  | NR |  | 7223890 | done |  | 2021-10-12 |  |  | 6 | 14 | 5 | [6 empty] | Yes
MEM-PRO-013-GRD-MFG-6431 | MP-BLOWER TO PHASE 3 GROUND FLAKE BIN | 300 Ton | 13-6431 | BLOW TO P3 GROUND FLAKE BIN |  | North | NR | NR | OK | OK | OK | NR | NR | NR | NR | NR | ok | OK | OK | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | NR |  |  |  |  | 2021-12-16 |  |  | 4 | 32 | 5 | [6 empty] | Yes
MEM-PRO-013-UTL-PRW-7283 | P3 - 90 DEG F WATER PUMP | P3 Curd B | 13-7283 | P3 - 90 DEG F WATER PUMP |  | North | NR | NR | OK | OK | NR | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | NR | ok | NR |  |  | OK |  | Gefft Data in June |  |  | 2021-12-15 |  |  |  | 28 | 5 | [6 empty] | Yes
MEM-PRO-013-XTR-1EX-9300 | MP3B-#3 1ST EXTRACTION CENTRIFUGE | P3 Curd B | 13-9300 | #3 1ST EXT FLOTTWEG CENTRIFU |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | 2 | 2 | 2 | ok | ok | ok | ok | NR | ok | NR |  |  | 3 | Motor has a high vibration that is a hamonic of a sub-synchronous fundamental. This may be related belt frequency. Inspect belts for wear and proper tension. Ensure sheaves aligned propelry and in good shape. | Outboard Decanter Bearing vibration has amplitude over 1 ips in the vertical direction. Unit likely needs to be cleaned and flushed. Rated as a CLASS III defect. | flush |  | 2021-12-15
MEM-PRO-013-XTR-1EX-9301 | MP3B-#2 1ST EXTRACTION CENTRIFUGE | P3 Curd B | 13-9301 | #2 1ST EXT FLOTTWEG CENTRIFU |  | North | OK | OK | OK | 2 | OK | OK | NR | NR | OK | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | NR | 2 | NR |  |  | 3 | Outboard end of the Flotweg has high 1 x rpm vibration with peak amplitude of near 1 ips. This is possible imbalance of the flotweg assembly. | Flottweg still has high 1 x rpm vibration. Imbalance may be the culprit. | flush |  | 2021-12-15 |  |  |  | 16 | #N/A
MEM-PRO-013-XTR-1EX-9302 | MP3B-#1 1ST EXTRACTION CENTRIFUGE | P3 Curd B | 13-9302 | #1 1ST EXT FLOTTWEG CENTRIFU |  | North | OK | OK | OK | OK | OK | OK | NR | NR | OK | OK | ok | OK | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | NR |  |  | 3 | Motor still has high 1 x flotwegg rpm vibration. This may be sheave related. Inspect sheaves for face run-out and misalingment as soon as practical. | Motor still has high 1 x flotwegg rpm vibration. This may be sheave related. Inspect sheaves for face run-out and misalingment as soon as practical. |  |  | 2021-12-15 |  |  |  | 16 | #N/A
MEM-PRO-013-XTR-2EX-9303 | MP3B-WEST 2ND EXTRACTION CENTRIFUGE | P3 Curd A | 13-9303 | #4 1ST EXT FLOTTWEG CENTRIFU |  | North | OK | OK | OK | NR | OK | NR | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  |  | 25 | #N/A |  | Gearbox
MEM-PRO-013-XTR-1EX-9308 | MP3B-1ST EXTRACT BOOSTER POT PUMP | P3 Curd A | 13-9308 | P3-1ST EXT BOOSTER POT PUMP |  | North | OK | OK | OK | NR | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 6 | 25 | #N/A |  | Gearbox
MEM-PRO-013-XTR-2EX-9309 | MP3B-2ND EXTRACTION FEED TANK PUMP | P3 Curd A | 13-9309 | 2ND EXT FEED TANK DIS PUMP |  | North | OK | OK | OK | NR | OK | OK | NR | NR | OK | ok | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 4 | 33 | #N/A |  | Gearbox
MEM-PRO-013-XTR-2EX-9314 | MP3B-2ND EXTRACT TANK PUMP | P3 Curd A | 13-9314 | 2ND EXT 5400 TANK DIS PUMP |  | North | OK | OK | OK | NR | OK | OK | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 4 | 16 | #N/A
MEM-PRO-013-XTR-3EX-9315 | MP3B-3RD EXTRACTION FEED TANK PUMP | P3 Curd B | 13-9315 | 3RD EXT FEED TANK PUMP |  | North | NR | NR | OK | NR | OK | NR | NR | NR | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-15 |  |  | 4 | 8 | 33
MEM-PRO-023-DIS-ALK-3770 | ALKALI/BLEND TANK DISCH PUMP | P1 Curd | 23-3770 | ALKALI/BLEND TANK DISCH PUMP |  | North | OK | OK | OK | OK | OK | OK | NR | NR | NR | NR | NR | NR | ok | NR | NR | OK | NR | NR | OK | ok | NR | NR |  |  | NR |  |  |  |  | 2021-11-09 |  |  |  | 16 | 28
MEM-PRO-024-UTL-WE2-5650 | MSS-WELL PUMP #2 (SOUTHEAST) | North Util | 24-5650 | WELL PUMP #2 (SOUTEAST) |  | North | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | NR | NR | OK | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 51
MEM-PRO-024-UTL-WE3-5651 | MSS-WELL PUMP #3 (CENTER EAST) | North Util | 24-5651 | WELL PUMP #3 (CENTER EAST) |  | North | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | OK | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 32 | 4 | [6 empty] | Yes
MEM-PRO-024-UTL-WE4-5652 | MSS-WELL PUMP #4 (EXISTING) (COOLING TOW | North Util | 24-5652 | WELL PUMP #4 (EXISTING) |  | North | NR | OK | OK | OK | OK | OK | NR | NR | NR | NR | NR | NR | NR | repair | repair | repair | repair | repair | repair | repair | NR | NR |  |  | NR |  | Defect. |  |  | 2020-09-01 |  |  |  | 16 | 4
MEM-PRO-024-UTL-WE6-5653 | MSS-WELL PUMP #6 (EXISTING) (NORTHWEST) | North Util | 24-5653 | WELL PUMP #6 (EXISTING) (NW) |  | North | OK | OK | OK | OK | OK | OK | OK | NR | OK | OK | ok | OK | OK | NR | ok | ok | ok | ok | NR | NR | NR | NR |  |  | OK |  |  |  |  | 2021-09-13 |  |  |  | 16 | 49 | [6 empty] | Yes
MEM-PRO-024-UTL-WE7-5654 | MSS-WELL PUMP #7 (EXISTING) (CENTER WEST | North Util | 24-5654 | WELL PUMP #7 (EXISTING) (CW) |  | North | NR | OK | OK | NR | OK | OK | OK | NR | OK | OK | ok | OK | OK | NR | ok | ok | ok | ok | NR | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 28
MEM-PRO-024-UTL-WE8-5655 | MSS-WELL PUMP #8 (EXISTING) (SOUTHWEST) | North Util | 24-5655 | WELL PUMP #8 (EXISTING) (SW) |  | North | OK | OK | OK | NR | OK | OK | NR | NR | OK | OK | NR | OK | OK | NR | ok | ok | ok | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 4
MEM-PRO-024-UTL-WE5-5658 | MSS-WELL PUMP #5 (PARKING LOT) | North Util | 24-5658 | WELL PUMP #5 (PARKING LOT) |  | North | OK | NR | NR | OK | OK | OK | NR | NR | OK | OK | ok | OK | OK | NR | ok | ok | NR | NR | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 4 | [6 empty] | Yes
MEM-PRO-024-UTL-WE1-5659 | MEM-PRO-024-UTL-WE1-5659 | North Util | 24-5659 | WELL PUMP #1 (SOUTEAST) |  | New North | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | ok | ok | ok | ok | 3 | NR | NR |  |  | NR |  | Motor data is starting to show signs of bearing issues. We will monitor this closely. Rated as a CLASS II defect for now. |  |  | 2021-11-08 |  |  |  | 16 | 4 |  |  | yes | No motor picture |  |  | Yes
MEM-PRO-025-UTL-RBL-0001 | #2 BOILER SYSTEM | North Util | 25-0001 | BOILER COMBUSTION FAN #2 |  | North | NR | OK | OK | NR | OK | OK | OK | NR | NR | OK | ok | OK | OK | ok | NR | OK | OK | OK | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 7 |  |  | yes | No motor picture |  |  | Yes
MEM-PRO-025-UTL-NDR-4277 | MSS-NE BFW PUMP | North Util | 25-4277 | NORTH EAST BFW PUMP |  | North | OK | OK | NR | OK | OK | OK | OK | NR | OK | OK | ok | OK | OK | ok | ok | ok | NR | ok | ok | ok | ok | NR |  |  | OK |  |  |  |  | 2021-12-14 |  |  |  | 16 | 4 |  |  | yes | No motor picture |  |  | Yes
MEM-PRO-025-UTL-NDR-4278 | MSS-C BFW PUMP | North Util | 25-4278 | CENTER BFW PUMP |  | North | OK | OK | OK | NR | OK | OK | OK | NR | OK | OK | ok | OK | OK | ok | ok | ok | ok | NR | ok | NR | NR | NR |  |  | NR |  |  |  |  | 2021-10-04 |  |  |  | 16 | 5 | [6 empty] | Yes
MEM-PRO-025-UTL-NDR-4280 | MSS-NW BFW PUMP | North Util | 25-4280 | WEST BFW PUMP |  | North | OK | OK | NR | OK | OK | OK | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | ok | ok | ok | ok | ok | NR |  |  | OK |  | NOT RUNNING |  |  | 2021-12-14 |  |  |  | 16 | 4 | [6 empty] | Yes
MEM-PRO-014-UTL-CSY-3545 | MSP-N BOGEY ENZYME FEED PUMP | South Util | 14-3545 | MSP-N BOGEY ENZYME FEED PUMP |  | New South | [29 empty] | 2021-12-02 |  |  | 8 | 8 | 28 | bar: NR to NR
MEM-PRO-014-UTL-CWS-4103 | MSP-Cooling Tower N FAN | South Util | 14-4103 | MSP COOLING TOWER N.FAN A |  | New South | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | repair | repair | repair | repair | NR | NR |  |  |  |  | FIXED 12-6-21 |  |  | #N/A |  |  |  | 8 | 28
MEM-PRO-014-UTL-CWS-4104 | MSP-COOLING TOWER S FAN | South Util | 14-4104 | MSP COOLING TOWER S.FAN B |  | New South | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | repair | repair | repair | repair | NR | NR |  |  |  |  | FIXED 12-6-21 |  |  | #N/A |  |  |  | 16 | 51
MEM-PRO-014-UTL-CWS-4111 | MSP-COOLING TOWER WATER PUMP | South Util | 14-4111 | E COOL TOWER WTR CIRC PUMP |  | South | NR | NR | NR | NR | NR | NR | OK | NR | NR | OK | NR | NR | NR | ok | OK | ok | NR | ok | ok | ok | ok | NR |  |  |  |  | Get Data in June |  |  | 2021-12-02 |  |  |  | 16 | 16
MEM-PRO-014-UTL-CWS-4113 | MSP-COOLING TOWER WATER PUMP (STANDBY) | South Util | 14-4113 | CT WATER PUMP STANDBY |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | ok | NR | ok | ok | ok | ok | NR | [7 empty] | 2021-12-02 |  |  |  | 16 | 4
MEM-PRO-014-UTL-CWS-4114 | MSP-COOLING TOWER WATER PUMP | South Util | 14-4114 | W COOL TOWER WATER CIRC PUMP |  | South | OK | OK | NR | OK | OK | OK | NR | NR | NR | NR | NR | NR | 4 | 4 | OK | ok | ok | ok | ok | ok | ok | NR |  |  |  |  | Motor has still has strong rotor bar passing frequency vibrations. No immediate concern. Rated a Class I Defect. |  |  | 2021-12-02
MEM-PRO-014-UTL-IAS-4126 | MSP-E.300 HP AIR COMPRESSOR | South Util | 14-4126 | MSP-E.300 HP AIR COMPRESSOR |  | South | OK | OK | NR | OK | OK | OK | OK | NR | NR | OK | ok | OK | OK | ok | OK | ok | ok | ok | ok | ok | ok | NR | [7 empty] | 2021-12-02
MEM-PRO-014-UTL-IAS-4127 | MSP-WEST AIR COMPRESSOR | South Util | 14-4127 | MSP-#2 WEST AIR COMPRESSOR |  | South | OK | OK | NR | OK | OK | OK | OK | NR | NR | OK | ok | OK | 4 | ok | OK | ok | ok | ok | ok | ok | ok | NR |  |  |  |  | Possible early bearing defects in the motor. We will watch for changes. Rated a Class I Defect. |  |  | 2021-12-02
MEM-PRO-014-UTL-CHS-4160 | MSP-CHILL WTR SUPPLY PUMP #3 | South Util | 14-4160 | MSP-CHILL WTR SUPPLY PUMP #3 |  | South | OK | OK | NR | 3 | 3 | OK | OK | NR | NR | OK | NR | NR | OK | NR | 2 | 2 | 2 | WR | WR | 1 | 4 | NR |  |  |  |  | Motor still shows strong 1x and 2x RPM vibrations. A 3x RPM vibration is also present in the axial. Inspect the drive train for wear and alignment. Check the structure and fasteners. Rated a Class III Defect. |  | #VALUE! | 2021-11-30 |  |  | 6 | 16 | 4
MEM-PRO-014-UTL-CHS-4161 | MSP-CHILL WTR SUPPLY PUMP #2 (STANDBY) | South Util | 14-4161 | CHILL WTR SUP PMP #2 STANDBY |  | South | OK | OK | NR | OK | OK | OK | OK | NR | NR | 2 | 3 | 3 | 3 | 1 | 3 | 3 | 3 | ok | ok | ok | 4 | NR |  |  |  |  | Elevated 1x RPM vibration in the motor. Check the unit base, fasteners, coupling and alignment as time allows. |  |  | 2021-12-02 |  |  | 6 | 16 | 4
MEM-PRO-014-UTL-CHS-4162 | MSP-CHILL WTR SUPPLY PUMP #1 | South Util | 14-4162 | MSP-#1 CHILL WTR SUPPLY PUMP |  | South | OK | OK | NR | OK | OK | OK | OK | NR | NR | OK | ok | OK | OK | ok | OK | 4 | 4 | ok | ok | ok | ok | NR |  |  |  |  | Motor vibration data still shows elevated 1x and 2x RPM vibrations. Inspect the drive train for wear and alignment. Check the motor fan, structure, and fasteners. Rated a Class I Defect. |  |  | 2021-12-02 |  |  | 6 | 16 | 4
MEM-PRO-014-STS-ALK-5110 | MSS-ALKALI TRANSFER STANDBY PUMP | South Util | 14-5110 | ALKALI TRANSFER STANDBY PUMP |  | New South | [29 empty] | 2021-12-02 |  |  | 4 | 16 | 4 | bar: NR to NR
MEM-PRO-014-UTL-CSY-9177 | MSP-STARCH WET-IN DISCHARGE PUMP | South Util | 14-9177 | STARCH WET-IN DISCHARGE PUMP |  | New South | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | repair | repair | repair | repair | ok | NR | [7 empty] | 2021-12-02 |  |  | 6
MEM-PRO-015-UTL-CWS-4103 | MS2P-COOLING TOWER N FAN | South Util | 15-4103 | MS2P COOLING TOWER N.FAN |  | New South | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | repair | repair | repair | repair | NR | NR | [7 empty] | 2021-01-19 |  |  |  | 16 | 36
MEM-PRO-015-UTL-CWS-4104 | MS2P-COOLING TOWER S FAN | South Util | 15-4104 | MS2P COOLING TOWER S.FAN |  | New South | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | Repair | repair | repair | repair | repair | NR | NR | [7 empty] | #N/A |  |  |  | 8 | 4
MEM-PRO-015-UTL-CWS-4111 | MS2P-COOLING TOWER E WATER PUMP | South Util | 15-4111 | COOLING TOWER E WATER PUMP |  | South | NR | OK | NR | 3 | 3 | NR | OK | NR | NR | OK | 4 | 4 | NR | NR | OK | 4 | 3 | bad data | bad data | 3 | 3 | NR |  |  |  |  | The motor bearings vibrations are still showing signs of distress. | 7259268 | #VALUE! | 2021-12-02 |  |  |  | 8 | 4
MEM-PRO-015-UTL-CWS-4112 | MS2P UT COOL TOWER W. PUMP B&G 1510 | South Util | 15-4112 | MS2P #2 UT COOL TOWER W PUMP |  | South | NR | NR | NR | NR | NR | OK | NR | NR | NR | OK | 3 | 2 | 2 | 3 | 3 | NR | ok | ok | ok | ok | ok | NR |  |  |  |  | Motor has elevated 1x RPM vibration. Inspect the motor drivetrain for wear and alignment. Check the motor cooling fan. As always, check the fasteners and structures. Rated a Class II Defect. |  |  | 2021-12-02 |  |  |  | 16 | 4
MEM-PRO-015-UTL-CWS-4113 | MS2P-COOLING TOWER CTR WTR PUMP | South Util | 15-4113 | COOLING TOWER CTR WTR PUMP |  | South | OK | NR | NR | NR | NR | OK | OK | NR | NR | OK | ok | NR | OK | ok | OK | OK | OK | OK | ok | ok | ok | NR |  |  |  |  | Get Data in June |  |  | 2021-12-02 |  |  |  | 16 | 4
MEM-PRO-015-UTL-CWS-4114 | MEM-PRO-015-UTL-CWS-4114 | South Util | 15-4114 | #1 COOLING TOWER WATER PUMP |  | New South | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | OK | repair | repair | repair | repair | NR | NR | [7 empty] | 2021-07-15 |  |  |  | 16 | 4
MEM-PRO-015-UTL-IAS-4126 | MS2P-E. 400 HP AIR COMPRESSOR | South Util | 15-4126 | MS2P-E 400 HP AIR COMPRESSOR |  | South | OK | OK | NR | OK | ok | OK | OK | NR | NR | OK | ok | OK | OK | ok | OK | OK | OK | OK | OK | ok | ok | NR | [7 empty] | 2021-12-02 |  |  |  | 16 | 4
MEM-PRO-015-UTL-IAS-4127 | MS2P-W. 400 HP AIR COMPRESSOR | South Util | 15-4127 | MS2P-W 400 HP AIR COMPRESSOR |  | South | OK | NR | NR | OK | OK | OK | 1 | NR | NR | OK | ok | OK | OK | NR | NR | OK | OK | OK | OK | ok | ok | NR | [7 empty] | 2021-12-02 |  |  |  | 16 | 4
MEM-PRO-015-UTL-CHS-4160 | MS2P-WEST CHILLED WATER SUPPLY PUMP | South Util | 15-4160 | W CHILLED WATER SUPPLY PUMP |  | South | NR | OK | NR | OK | 3 | WR | OK | NR | NR | OK | NR | OK | OK | NR | OK | OK | OK | OK | OK | ok | ok | NR |  |  |  |  | Base issues |  |  | 2021-12-02
MEM-PRO-015-UTL-CHS-4161 | MS2P-CENTER CHILLED WATER SUPPLY PUMP | South Util | 15-4161 | CENTER CHILL WTR SUPPLY PUMP |  | South | OK | OK | NR | NR | 3 | WR | NR | NR | NR | OK | 2 | 2 | NR | 1 | 2 | 3 | 4 | WR | OK | ok | ok | NR |  |  |  |  | Motor vibration data shows a drop in 1x and 2x RPM vibrations. Check the unit speed to insure correct analysis. Inspect the drive train for wear and alignment. Check the structure and fasteners. Rated a Class I Defect. |  |  | 2021-12-02 |  |  |  | 8 | 4
MEM-PRO-015-UTL-CHS-4162 | MS2P-EAST CHILLED WATER SUPPLY PUMP | South Util | 15-4162 | E CHILLED WATER SUPPLY PUMP |  | South | NR | NR | NR | OK | 3 | WR | OK | NR | NR | OK | NR | NR | OK | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | NR |  |  |  |  | Check the unit fasteners, coupling, and alignment | 7248790 | #VALUE! | 2021-12-02 |  |  |  | 8 | 4
MEM-PRO-014-FED-FED-3837 |  | UE - MSP Feed Dryer | 14-3837 | MSP-FEED DRYER DRY FEED RECVR DISCH RFV |  | UE-MSP-Feed | [5 empty] | OK: 3 |  |  |  |  | gearbox high ultrasound readings | 7264076 | UE | #N/A
Need to add MS2P 15-3087 took dryer down. Add to UE and critial list 6 hours.
15-3047- add to ue Route and criticality 6 down on dryer
Removed from service in July 2021
MEM-PRO-013-BGY-FCS-6274 | MP3B-S 600 VAC VACUUM PUMP (EAST) |  | 13-6274 | MP3B-S 600 VAC VACUUM PUMP E |  | North | OK | NR | OK | 2 | 4 | 4 | OK | NR | 4 | NR | ok | OK | ok | NR | NR | NR | NR | NR | NR | NR | NR | NR |  |  |  |  | coupling |  | #VALUE! | 2021-03-08 |  |  | 0 | 8 | 49
can not reach and not on critial list.
MEM-PRO-025-UTL-1BL-4275 | MEM-PRO-025-UTL-1BL-4275 |  | 25-4275 | BOILER COMBUSTION FAN #1 |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
moved to UE | #N/A |  | 15-5506 | DRY INGREDIENT SURGE RFV |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-GRD-MFG-3012 | MSP - NORTH GRINDER FEED RFV |  | 14-3012 | MSP-NORTH GRINDER FEED RFV |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-GRD-MFG-3020 | MSP - N. GRND SRG HPPR DSCH RFV |  | 14-3020 | N. GRND SRG HPPR DSCH RFV |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-GRD-MFG-3025 | MSP - SOUTH GRINDER FEED RFV |  | 14-3025 | MSP-SOUTH GRINDER FEED RFV |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-GRD-MFG-3047 | MSP-S. DUST COLLECTOR DSCH RFV #2 |  | 14-3047 | S.DUST COLLECTOR DSCH RFV 2 |  | New South | NR | NR | NR | NR | NR | [21 empty] | moved to UE |  |  | #N/A | bar: WR to NR
MEM-PRO-014-FED-FED-2369 | MSP-FIBRIM LOADOUT BLOWER | #N/A | 14-2369 | MSP-FIBRIM LOADOUT BLOWER |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
#N/A
MEM-PRO-014-XTR-1EX-3112 | MSP-1ST EXTRACTION TANK AGITATOR | #N/A | 14-3112 | 1ST EXTRACTION TANK AGITATOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | 2021-06-30 | bar: WR to NR
MEM-PRO-014-BGY-TIL-3505 | MSP-N BOGEY MC75 FEED PUMP | #N/A | 14-3505 | MSP-N BOGEY MC75 FEED PUMP |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-UTL-CSY-3545 | MSP-N BOGEY ENZYME FEED PUMP | #N/A | 14-3545C | MSP-N BOGEY ENZYME FEED PUMP |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-SPR-PRC-3644 | MSP-MAIN DRYER BODY RFV | #N/A | 14-3644 | MSP-MAIN DRYER BODY RFV |  | New South | NR | NR | NR | NR | NR | [24 empty] | 2021-06-25 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3647 | MSP-DRYER BOTTOM PRODUCT SCREENER RFV | #N/A | 14-3647 | DRYER BOTTOM PROD SCREEN RFV |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-SPR-PRC-3650 | MSP-PRODUCT COLLECTOR RFV | #N/A | 14-3650 | MSP-PRODUCT COLLECTOR RFV |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-UTL-CSY-3906 | MSP-PROCESS DEFOAMER PUMP | #N/A | 14-3906 | MSP-PROCESS DEFOAMER PUMP |  | New South | NR | NR | NR | NR | NR | [24 empty] | 2021-06-30 | bar: WR to NR
MEM-PRO-014-UTL-CSY-3906 | MSP-PROCESS DEFOAMER PUMP | #N/A | 14-3906C | MSP-PROCESS DEFOAMER PUMP |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-UTL-CHS-4159 | MSP-CHILL WTR SUPPLY PUMP #4 | #N/A | 14-4159 | MSP-CHILL WTR SUPPLY PUMP #4 |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-WEI-WIS-4303 | MSP-COUNTER CURRENT TANK AGITATOR | #N/A | 14-4303 | COUNTER CURT TANK AGITATOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | 2021-06-30 | bar: WR to NR
MEM-PRO-014-IDN-IDF-4704 | MSP-CAUSTIC ADJ TK AGITATOR | #N/A | 14-4704 | MSP-CAUSTIC ADJ TK AGITATOR |  | New South | NR | NR | NR | NR | NR | [21 empty] | product dependent |  |  | 2021-06-30 | bar: WR to NR
MEM-PRO-014-UTL-CSY-4711 | MSP-PASTEURIZATION TANK AGITATOR | #N/A | 14-4711 | PASTEURIZATION TANK AGITATOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-PKG-PAK-4902 | MSP-BLENDER SURGE BIN RFV | #N/A | 14-4902 | MSP-BLENDER SURGE BIN RFV |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-STS-ALK-5101 | MSP-ALKALI TANK AGITATOR | #N/A | 14-5101 | MSP-ALKALI TANK AGITATOR |  | New South | NR | NR | NR | NR | NR | [21 empty] | does not exisit in plant |  |  | #N/A | bar: WR to NR
MEM-PRO-023-DIS-ALK-5110 | MSS-ALKALI TRANSFER STANDBY PUMP | #N/A | 14-5110C | ALKALI TRANSFER STANDBY PUMP |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-IDN-HYS-5679 | MSP-SLAM SURGE TANK AGITATOR | #N/A | 14-5679 | MSP-SLAM SURGE TANK AGITATOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-UTL-CSY-9174 | MSP-STARCH AGITATOR | #N/A | 14-9174 | MSP-STARCH AGITATOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-UTL-CSY-9174 | MSP-STARCH AGITATOR | #N/A | 14-9174C | MSP-STARCH AGITATOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-014-UTL-CSY-9177 | MSP-STARCH WET-IN DISCHARGE PUMP | #N/A | 14-9177C | STARCH WET-IN DISCHARGE PUMP |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-015-XTR-2EX-3203 | MEM-PRO-015-XTR-2EX-3203 | #N/A | 15-3203 | 6 CENT SLUDGE TRANS CONVEYOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-015-IDN-IDF-3435 | MS2P-E VACUUMIZER FEED PUMP | #N/A | 15-3435 | 2P EAST BOGEY FP |  | New South | NR | NR | NR | NR | NR | [21 empty] | can not get |  |  | #N/A | bar: WR to NR
MEM-PRO-015-UTL-CSY-3497 | MS2P-ENZYME WORK TANK AGITATOR | #N/A | 15-3497 | ENZYME WORK TANK AGITATOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-015-FED-FED-3866 | MS2P-N FEED DRYER FILTER SCREW CONVEYOR | #N/A | 15-3866 | N FD FILTER SCREW CONVEYOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-015-FED-FED-3888 | MS2P-S FEED DRYER FILTER SCREW CONVEYOR | #N/A | 15-3888 | S FD FILTER SCREW CONVEYOR |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-015-FED-SLT-4102 | MS2P-BELT PRESS SCREW CONVEYOR #2 | #N/A | 15-4102 | BELT PRESS SCREW CONVEYOR #2 |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-015-FED-BLP-4109 | MS2P-BELT PRESS DISCHARGE SCREW CONV #4 | MS2P Feed Dryer | 15-4109 | BELT PRES DISCH SCREW CONV 4 |  | New South | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-011-HPF-SDF-4925 | MP1-#2 SSMG HI-PRESS DRYER FEED PUMP | P1 Curd | 11-4925-0 | MP1-#2 SSMG DRYER FEED PUMP |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-011-HPF-SDF-4930 | MP1-#1 SSMG HI-PRESS DRYER FEED PUMP | P1 Curd | 11-4930-0 | MP1-#1 SSMG DRYER FEED PUMP |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-013-SPR-DRY-2473 | M3PB-DRYER BOTTOM RFV | P3 Dryer | 13-2473 | M3PB-DRYER BOTTOM RFV |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-013-SPR-DRY-2481 | MP3B-N CYCLONE DISCHARGE RFV | P3 Dryer | 13-2481 | MP3B-N CYCLONE DISCHARGE RFV |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-013-SPR-DRY-2489 | MP3B-S CYCLONE DISCHARGE RFV | P3 Dryer | 13-2489 | MP3B-S CYCLONE DISCHARGE RFV |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-013-SPR-DRY-2522 | MP3B-S BAGHOUSE DISCHARGE RFV | P3 Dryer | 13-2522 | P3B-S BAGHOUSE DISCHARGE RFV |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | [27 empty] | HS pinion 37T HS Gear 56T Intmd Pinion 15T Intmd gear 94T LS Pinion 18T LS Gear 75T | bar: WR to NR
MEM-PRO-013-FED-FED-3021 | MP3B-FEED DRYER VENT FILTER COLLCTOR RFV | P3 Alget Dryer | 13-3021 | FD VENT FILTER COLLECTOR RFV |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-013-FED-FED-3031 | MP3B-FD DISCHARGE TO FEED LOADOUT RFV | P3 Alget Dryer | 13-3031 | FD DISCH TO FEED LOADOUT RFV |  | New North | NR | NR | NR | NR | NR | [24 empty] | 2021-06-16 | bar: WR to NR
MEM-PRO-013-BGY-TIL-6194 | MP3-N MC75 FEED PUMP | P3 Curd B | 13-6194 | MP3-N MC75 FEED PUMP |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-013-BGY-TIL-6197 | MP3-S MC75 FEED PUMP | P3 Curd B | 13-6197 | MP3-S MC75 FEED PUMP |  | New North | NR | NR | NR | NR | NR | [24 empty] | #N/A | bar: WR to NR
MEM-PRO-013-CHL-REW-1451 | WET REWORK DISCHARGE PUMP | P3 Curd B | 13-1451 | WET REWORK DISCHARGE PUMP |  | North | NR | NR | OK | NR | NR | [21 empty] | Get Data in June |  | #VALUE! | #N/A |  |  | 0 | 8 | 23 | bar: WR to NR
=100/367
MEM-PRO-015-HPF-SDF-3583 |  |  |  | #N/A |  | IB Wireless | 182 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-015-HPF-SDF-3587 |  |  |  | #N/A |  | IB Wireless | 183 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-015-HPF-SDF-3594 |  |  |  | #N/A |  | IB Wireless | 184 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-015-HPF-SDF-3598 |  |  |  | #N/A |  | IB Wireless | 185 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-014-UTL-IAS-4120 |  |  |  | #N/A | [30 empty] | #VALUE! | #VALUE!
MEM-PRO-014-HPF-SDF-3583 |  |  |  | #N/A |  | IB Wireless | 178 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-014-HPF-SDF-3587 |  |  |  | #N/A |  | IB Wireless | 179 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-014-HPF-SDF-3594 |  |  |  | #N/A |  | IB Wireless | 180 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-014-HPF-SDF-3598 |  |  |  | #N/A |  | IB Wireless | 181 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-011-HPF-SDF-4925 |  |  |  | #N/A |  | IB Wireless | 172 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-011-HPF-SDF-4930 |  |  |  | #N/A |  | IB Wireless | 173 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-010-UTL-IAS-1401 |  |  |  | #N/A
MEM-PRO-010-UTL-IAS-4142 |  |  |  | #N/A
MEM-PRO-010-UTL-IAS-4142 |  |  |  | #N/A
MEM-PRO-010-UTL-IAS-0890 |  |  |  | #N/A
MEM-PRO-013-HPF-SDF-6170 |  |  |  | #N/A |  | IB Wireless | 174 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-013-HPF-SDF-6171 |  |  |  | #N/A |  | IB Wireless | 175 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-013-HPF-SDF-6172 |  |  |  | #N/A |  | IB Wireless | 176 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
MEM-PRO-013-HPF-SDF-6173 |  |  |  | #N/A |  | IB Wireless | 177 and 32 on the number of teeth on each gear | [27 empty] | #VALUE! | #VALUE!
Add to current equipment more points | [40 empty] | 0
Add to Wireless program not currently on list
Jason King, jason.king@emerson.com, +18653992446, Machinery Health Solutions Manager
Name new database as IFF-Vibe database update-2021
Equipment we never got readings on. | [40 empty] | 0
MEM-PRO-015-IDN-IDF-3435 | MS2P-E VACUUMIZER FEED PUMP | #N/A | 15-3435 |  |  | ???? | NR | NR | NR | NR | NR | [21 empty] | remote access ? |  |  | #VALUE! |  |  | 5 | 16 | 28 | bar: WR to NR
MEM-PRO-025-UTL-1BL-4275 | BOILER COMBUSTION FAN #1 | MPU - MAIN PLANT UTILITIES | 25-4275 |  |  | ??? | NR | NR | NR | NR | NR | [24 empty] | #VALUE! |  |  |  | 8 | #N/A | bar: WR to NR
MEM-PRO-010-UTL-CHS-9306 | Main Plant Chill Water Pump #2 | P3 CURD | 10-9306 |  |  | Wireless | NR | NR | NR | NR | NR | [21 empty] | remote access |  |  | #VALUE! |  |  | 0 | 16 | #N/A | bar: WR to NR
MEM-PRO-015-UTL-CWS-4103 | MS2P-COOLING TOWER N FAN | SOUTH PLANT UTILITIES | 15-4103 |  |  | South | NR | NR | NR | NR | NR | NR | NR | NR | NR | WR2 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR |  |  |  |  | Need to fix wires - Need to go into cooling tower when down and insure that all accels are attached to the equipment, and wires are not damaged all the way from accel to the termination box. Need to have vibe tool verify each accel is reading correctly to verify work as you go from accel to accel. | 7208385 |  | #VALUE! |  |  | 0 | 24 | 4
MEM-PRO-015-UTL-CWS-4104 | MS2P-COOLING TOWER S FAN | SOUTH PLANT UTILITIES | 15-4104 |  |  | South | NR | NR | NR | NR | NR | [21 empty] | Need to fix wires | 7208385 |  | #VALUE! |  |  | 0 | 24 | 37 | bar: WR to NR
MEM-PRO-014-UTL-CWS-4104 | MSP-COOLING TOWER S FAN | SOUTH PLANT UTILITIES | 14-4104 |  |  | South | NR | NR | NR | NR | NR | [21 empty] | Need to fix wires | 7208385 |  | #VALUE! |  |  | 0 | 24 | #N/A | bar: WR to NR
MEM-PRO-014-UTL-CWS-4113 | MSP-COOLING TOWER WATER PUMP (STANDBY) | SOUTH PLANT UTILITIES | 14-4113 |  |  | Wireless | NR | NR | NR | NR | NR | NR | NR | NR | NR | WR2 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR |  |  |  |  | Get Data in June |  |  | #VALUE! |  |  | 0 | 16 | 4
MEM-PRO-015-UTL-CWS-4114 | MS2P-COOLING TOWER W WATER PUMP | SOUTH PLANT UTILITIES | 15-4114 |  |  | South | NR | NR | NR | NR | NR | [21 empty] | Pump disassembled |  |  | #VALUE! |  |  | 0 | 16 | 21 | bar: WR to NR
MEM-PRO-014-UTL-PRW-4203 | MSP-HOT WATER PUMP TO H-HEATER | MSP CIP | 14-4203 |  |  | Wireless | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 3 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR |  |  |  |  | Pump data shows a few harmonics of shaft speed and overall velocity is near 0.5”/second velocity peak. Check the inboard bearing for looseness as well as the base and fasteners. Inspect the coupling and alignment too. Rated a Class II Defect. | 7237532 |  | #VALUE! |  |  | 0 | 16 | 18
MEM-PRO-014-SPR-PRC-5212 | MSP-DRY REWORK FAN | #N/A | 14-5212 |  |  | ??? | NR | NR | NR | NR | NR | [21 empty] | Get Data in June |  |  | #VALUE! |  |  | 0 | 16 | #N/A | bar: WR to NR
MEM-PRO-014-PKG-BLD-3697 | MSP-PACKAGING ASPIRATION FILTER RCVR FAN | #N/A | 14-3697 |  |  | ??? | NR | NR | NR | NR | NR | [21 empty] | Get Data in June |  |  | #VALUE! |  |  | 0 | 16 | #N/A | bar: WR to NR
MEM-PRO-010-SLM-AEQ-5681 | MS2P-SLAM SURGE PUMP #1 | #N/A | 10-5681 |  |  | ??? | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 4 | NR | NR | NR | NR | NR | NR | NR | NR | NR |  |  |  |  | Non-synchronous pump vibrations. Early bearing defects. Rated a Class I Defect. |  |  | #VALUE! |  |  | 0 | 15 | #N/A
MEM-PRO-014-CIP-DAC-4050 | MSP-CIP SUPPLY PUMP TO DRYER #1 | MSP CIP | 14-4050 |  |  | Wireless | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 3 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR |  |  |  |  | First data on unit shows a 1x and 2x RPM vibration in the pump with overall velocity at around 0.5”/second peak. Acceleration data also indicates some cavitation. Inspect the coupling and shaft alignment first. We may suggest impeller inspection in the future. Rated a Class II Defect. | 7237533 |  | #VALUE! |  |  | 0 | 14 | #N/A
MEM-PRO-014-CIP-CAC-4028 | MSP-CIP SUPPLY FEED PUMP TO PREC. TANK | MSP CIP | 14-4028 |  |  | Wireless | NR | NR | NR | NR | NR | [21 empty] | CIP - need approval |  |  | #VALUE! |  |  | 0 | 16 | 18 | bar: WR to NR
MEM-PRO-014-CIP-CAC-4027 | MSP-CIP RINSE TANK FLOW VALVE TO 4027 | MSP CIP | 14-4027 |  |  | Wireless | NR | NR | NR | NR | NR | [21 empty] | CIP - need approval |  |  | #VALUE! |  |  | 0 | 16 | 18 | bar: WR to NR
MEM-PRO-014-UTL-PRW-4209 | MSP-90 DEG PROCESS STANDBY WTR PUMP | MSP CIP | 14-4209 |  |  | Wireless | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR | 3 | NR | NR | NR | NR | NR | NR | NR | NR | NR | NR |  |  |  |  | Pump data shows a few harmonics of shaft speed and overall velocity is near 0.5”/second velocity peak. Check the inboard bearing for looseness as well as the base and fasteners. Inspect the coupling and alignment too. Rated a Class II Defect. | 7237531 |  | #VALUE! |  |  | 0 | 16 | 18
|  | #N/A | - |  |  | North | OK | NR | NR | NR | NR | [21 empty] | Get Data in June |  |  | #VALUE! |  |  | 0 | 16 | 15 | bar: WR to NR
|  | #N/A | - |  |  | North | OK | NR | NR | NR | NR | [21 empty] | Get Data in June |  |  | #VALUE! |  |  | 0 | 16 | #N/A | bar: WR to NR
MEM-PRO-011-WSH-WRE-4435 | MP1-CENTRIFUGE FEED PUMP | P1 CURD | 11-4435 |  |  | North | OK | OK | NR | OK | WR | [24 empty] | #VALUE! |  |  | 0 | 16 | 5 | [6 empty] | Yes | bar: WR to NR
MEM-PRO-024-UTL-WE1-5659 | MSS-WELL PUMP #1 (SOUTHEAST) | MPU - MAIN PLANT UTILITIES | [30 empty] | copy from (MEM-PRO-024-UTL-WE2-5650)
Removed from routes
MEM-PRO-014-CIP-DAC-4051 | MSP-CIP SUPPLY PUMP TO DRYER #2 | MSP CIP | 14-4051 |  |  | Wireless | NR | NR | NR | NR | NR | [21 empty] | CIP - need approval |  |  | #VALUE! |  |  | 0 | 16 | #N/A | bar: WR to NR
MEM-PRO-014-SPR-PRC-3646 | MSP-DRYER BOTTOM PRODUCT SCREENER | [39 empty] | 0
MEM-PRO-014-PKG-PAK-3720 | MSP-#1 AZO SCREENER SYSTEM | [10 empty] | NR: 0.77711 | [12 empty] | 0
[33 empty] | 0.71171 | [7 empty] | 0
0
MEM-PRO-010-UTL-PRW-2495 | MN-PLT STH 90 DEG WTR TK S. SUPPLY PUMP | [39 empty] | 0
MEM-PRO-010-UTL-PRW-2496 | MSS-MN PLT NORTH 90 DEG WTR TK N PUMP | [39 empty] | 0
MEM-PRO-010-UTL-PRW-2497 | MSS-MN PLT NORTH 90 DEG WTR TK C PUMP | [39 empty] | 0
[12 empty] | NR: 0.22667 | [12 empty] | 0
0
MEM-PRO-010-UTL-IAS-1401 | MSS-#6 200 HP AIR COMPRESSOR | [39 empty] | 0
MEM-PRO-010-UTL-IAS-1402 | MSS-AIR RECEIVER FOR #6 AIR COMPRESSOR | [39 empty] | 0
MEM-PRO-010-UTL-IAS-2100 | MSS-N PLANT #2 AIR COMPRESSOR 125 HP | [39 empty] | 0
MEM-PRO-010-UTL-IAS-2105 | MSS-N PLANT #1 AIR COMPRESSOR 100 HP | [39 empty] | 0
MEM-PRO-010-UTL-IAS-4142 | MSS-800T 100 HP CTR AIR COMPRESSOR | [39 empty] | 0
MEM-PRO-010-UTL-IAS-0820 | MSS-N PLANT #3 AIR COMPRESSOR 100 HP | [39 empty] | 0
MEM-PRO-010-UTL-IAS-0890 | MSS-N PLANT #4 AIR COMPRESSOR 200 HP | [39 empty] | 0
MEM-PRO-010-UTL-IAS-0891 | MSS-N PLANT #5 AIR COMPRESSOR 150 HP | [39 empty] | 0
MEM-PRO-010-BLD-IAS-0893 | MRAL-25 HP AIR COMPRESSOR | [39 empty] | 0
MEM-PRO-010-UTL-IAS-0893 | MRAL-25 HP AIR COMPRESSOR | [39 empty] | 0
MEM-PRO-014-UTL-IAS-4126 | MSP-E.300 HP AIR COMPRESSOR | [39 empty] | 0
MEM-PRO-014-UTL-IAS-4127 | MSP-WEST AIR COMPRESSOR | [39 empty] | 0
MEM-PRO-014-UTL-IAS-4120 | MSP-40 HP S 800T AIR COMPRESSOR | [39 empty] | 0
MEM-PRO-015-UTL-IAS-4127 | MS2P-W. 400 HP AIR COMPRESSOR | [39 empty] | 0
MEM-PRO-015-UTL-IAS-4126 | MS2P-E. 400 HP AIR COMPRESSOR | [39 empty] | 0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
|  | SOUTH PLANT UTILITIES | delete |  |  | South | NR | NR | NR | NR | NR | [21 empty] | Need to fix wires | 7208385 |  | #VALUE! |  |  | 0 | 24 | 37 | bar: WR to NR
MEM-PRO-015-UTL-CWS-4104 | MS2P-COOLING TOWER S FAN | #N/A | delete |  |  | South | NR | NR | NR | NR | NR | [21 empty] | Need to fix wires | 7208385 |  | #VALUE! |  |  | 0 | 8 | #N/A | bar: WR to NR
MEM-PRO-015-UTL-CWS-4103 | MS2P-COOLING TOWER N FAN | #N/A | delete |  |  | South | NR | NR | NR | NR | NR | [21 empty] | Need to fix wires | 7208385 |  | #VALUE! |  |  | 0 | 8 | #N/A | bar: WR to NR
0
0
0
0
MEM-PRO-011-XTR-1EX-4159 | [5 empty] | North | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 16 | #N/A | bar: WR to NR
MEM-PRO-014-WEI-WIS-3038 | MSP-DUST COLLECTOR #3 ROTARY VALVE |  |  |  |  | South | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 16 | #N/A | bar: WR to NR
MEM-PRO-011-CON-1SC-4565 | MP1-CENTRIFUGE PROD POT MOYNO DISCH PUMP |  |  |  |  | South | OK | NR | NR | OK | OK | [21 empty] | Get Data in June |  |  | #VALUE! |  |  |  | 16 | #N/A | bar: WR to NR
MEM-PRO-014-FED-SLT-3203 | MSP-3RD EXT SLUDGE CONV FROM #4 SHARP |  |  |  |  | South | NR | OK | NR | OK | OK | [24 empty] | #VALUE! |  |  |  | 8 | #N/A | bar: WR to NR
MEM-PRO-011-IDN-IDF-4777 | MP1-NEUTRAL TK DISCH PUMP, REDUCER & MOT |  |  |  |  | South | OK | OK | NR | OK | OK | [24 empty] | #VALUE! |  |  |  | 16 | #N/A | bar: WR to NR
MEM-PRO-011-XTR-2EX-4265 | MP1-2ND EXTRACTION FEED POT DISCH PUMP |  |  |  |  | South | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 16 | #N/A | bar: WR to NR
MEM-PRO-014-FED-SLT-3203 | MSP-3RD EXT SLUDGE CONV FROM #4 SHARP |  |  |  |  | South | NR | OK | NR | OK | OK | [24 empty] | #VALUE! |  |  |  | 8 | #N/A | bar: WR to NR
MEM-PRO-014-WEI-WIS-3038 | MSP-DUST COLLECTOR #3 ROTARY VALVE |  |  |  |  | South | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 0 | #N/A | bar: WR to NR
MEM-PRO-011-CON-1SC-4510 | MP1-#1 CONCENTRATOR DISCH PUMP |  |  |  |  | South | NR | NR | NR | OK | OK | [21 empty] | Get Data in June |  |  | #VALUE! |  |  |  | 16 | #N/A | bar: WR to NR
MEM-PRO-011-XTR-2EX-4341 | MP1-1ST EXTRACTION CENTRIFUGE |  |  |  |  | South | NR | NR | NR | OK | OK | [21 empty] | Get Data in June |  |  | #VALUE! |  |  |  | 16 | #N/A | bar: WR to NR
MEM-PRO-011-XTR-2EX-9323 | MP1 2ND EXT DCNTR SLDG PUMP |  |  |  |  | South | NR | NR | NR | OK | OK | [21 empty] | Get Data in June |  |  | #VALUE! |  |  |  | 24 | #N/A | bar: WR to NR
MEM-PRO-013-IDN-IDF-6289 | MP3B - NEUT TK AGITATOR MTR |  |  |  |  | North | OK | NR | NR | OK | OK | [21 empty] | Wireless Recommended x2 |  |  | #VALUE! |  |  |  | 8 | #N/A | bar: WR to NR
MEM-PRO-015-UTL-PRW-4208 | MS2P-90 DEG F PROCESS WTR PUMP |  |  |  |  | South | NR | NR | NR | OK | OK | [21 empty] | CIP issue - |  |  | #VALUE! |  |  |  | 16 | #N/A | bar: WR to NR
0
0
0
0
MEM-PRO-015-SPR-DRY-8109 | MS2P-VF BAGHOUSE RFV | [5 empty] | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-013-IDN-IDF-6119 | MP3B-IDN FEED TANK AGITATOR | [5 empty] | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-013-IDN-HYS-6323 | MP3B-E BATCH TANK AGITATOR | [5 empty] | 3 | NR | NR | 3 | OK | [21 empty] | CAW R/R 115 TANK AGITATOR GEARBOX | 7177492 |  | Never | POK |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-013-IDN-HYS-6322 | MP3B-W BATCH TANK AGITATOR | [5 empty] | NR | NR | NR | OK | OK | [21 empty] | Wireless Recommended x2 |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-013-CHL-CCS-0182 | MP3B-N #3 CHILL TANK AGITATOR | [5 empty] | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-013-CHL-CCS-0181 | MP3B-S #4 CHILL TANK AGITATOR | [5 empty] | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-014-FED-SLT-3203 | MSP-3RD EXT SLUDGE CONV FROM #4 SHARP | [5 empty] | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-015-SPR-DRY-8100 | MS2P-VF BAGHOUSE EXHAUST FAN | [5 empty] | NR | NR | NR | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
0
0
0
MEM-PRO-013-PKG-PAK-2277 | MP3-ASP. PACKER FAN | [5 empty] | NR | NR | NR | OK | OK | [21 empty] | dELETEd |  |  | #VALUE! |  |  |  | 16 | 11 | bar: WR to NR
MEM-PRO-013-CON-CRE-0149 | MP3B-#1/#2 CONC PRODUCT POT PUMP | [5 empty] | OK | NR | NR | OK | OK | [21 empty] | DELETEd |  |  | #VALUE! |  |  |  | 16 | 15 | bar: WR to NR
MEM-PRO-013-CON-CRE-0166 | MP3B-#3/4 CONC PRODUCT POT PUMP | [5 empty] | OK | NR | NR | OK | OK | [21 empty] | DELETEd |  |  | #VALUE! |  |  |  | 16 | 15 | bar: WR to NR
MEM-PRO-013-UTL-LAL-7246 | MP3 (LAL LIME) CONC P5000 | [5 empty] | NR | NR | NR | OK | OK | [21 empty] | deLETEd |  |  | #VALUE! |  |  |  | 29 | 26 | bar: WR to NR
MEM-PRO-013-PKG-BLD-2190 | MP3B-BLENDER SEAL BLOWER | [5 empty] | OK | NR | NR | OK | OK | [21 empty] | DELETEd |  |  | #VALUE! |  |  |  | 16 | 16 | bar: WR to NR
0
0
MEM-PRO-014-CON-CRE-3344 | MSP-#2 CURD POT PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 26 | 44 | bar: WR to NR
MEM-PRO-010-CAL-HPO-4060 | MSS-CALPRO LIME BIN #8 COLL BLWBK FAN | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 18 | 44 | bar: WR to NR
MEM-PRO-010-OP1-AEQ-3333 | MP1-SCOTT DRYER BURNER CHAMBER | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 18 | 44 | bar: WR to NR
MEM-PRO-014-CON-CRE-4098 | MSP-#4 CURD POT PUMP | [5 empty] | NR | NR | OK | OK | OK | [24 empty] | #VALUE! |  |  |  | 18 | 44 | bar: WR to NR
MEM-PRO-014-CON-CON-3319 | MSP-#6 CENTRIFUGE CONC SLUDGE PUMP | [5 empty] | NR | NR | OK | OK | OK | [24 empty] | #VALUE! |  |  |  | 16 | 44 | bar: WR to NR
MEM-PRO-014-CON-CON-3321 | MSP-#7 CENTRIFUGE SLUDGE PUMP | [5 empty] | NR | NR | OK | OK | OK | [24 empty] | #VALUE! |  |  |  | 18 | 44 | bar: WR to NR
MEM-PRO-010-OP1-AEQ-3297 | MP1-SCOTT DRYER E. DCE SCREW CONVEYOR | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 18 | 44 | bar: WR to NR
MEM-PRO-011-WEI-WIS-4092 | MP1-ACRISON DCE VIBRATOR | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 18 | 44 | bar: WR to NR
[7 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 32 | #VALUE! | bar: WR to NR
MEM-PRO-014-HPF-SDF-3598 | MSP-#1 SSMG HI-PRESS DRYER FEED PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-014-HPF-SDF-3594 | MSP-#2 SSMG HI-PRESS DRYER FEED PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-014-HPF-SDF-3587 | MSP-#3 SSMG HI-PRESS DRYER FEED PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-014-HPF-SDF-3583 | MSP-#4 SSMG HI-PRESS DRYER FEED PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-013-HPF-SDF-6173 | MP3B-#1 SSMG HI-PRESS DRYER FEED PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | NOT ACCESSABLE |  |  | #VALUE! |  |  |  | 16 | 5 | bar: WR to NR
MEM-PRO-013-HPF-SDF-6172 | MP3B-#2 SSMG HI-PRESS DRYER FEED PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | NOT ACCESSABLE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-013-HPF-SDF-6171 | MP3B-#3 SSMG HI-PRESS DRYER FEED PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | NOT ACCESSABLE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-013-HPF-SDF-6170 | MP3B-#4 SSMG HI-PRESS DRYER FEED PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | NOT ACCESSABLE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-014-CON-CRE-4098 | MSP-#4 CURD POT PUMP | [5 empty] | NR | NR | OK | OK | OK | [24 empty] | #VALUE! |  |  |  | 16 | 13 | bar: WR to NR
MEM-PRO-010-CAL-HPO-4060 | MSS-CALPRO LIME BIN #8 COLL BLWBK FAN | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 14 | 13 | bar: WR to NR
MEM-PRO-014-CON-CRE-3344 | MSP-#2 CURD POT PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 16 | 43 | bar: WR to NR
MEM-PRO-010-OP1-AEQ-3333 | MP1-SCOTT DRYER BURNER CHAMBER | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | #VALUE! |  |  |  | 16 | 13 | bar: WR to NR
0
0
0
[7 empty] | NR | NR | OK | OK | OK | [21 empty] | NOT ACCESSABLE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
[7 empty] | NR | NR | OK | OK | OK | [21 empty] | NOT ACCESSABLE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
[7 empty] | NR | NR | OK | OK | OK | [21 empty] | NOT ACCESSABLE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-010-OPA-AEQ-1234 | MP1A-OIL TANK DISCHARGE VALVE | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-010-UTL-IAS-2105 | MSS-N PLANT #1 AIR COMPRESSOR 100 HP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-024-UTL-WE1-5659 | MSS-WELL PUMP #1 (SOUTHEAST) | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 8 | #VALUE! | bar: WR to NR
MEM-PRO-013-CON-CON-0098 | MP3B-#1 CONC CENT PRODUCT PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-013-CON-CON-0260 | MP3B-#2 CONC CENT PRODUCT PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-013-CON-CON-0281 | MP3B-#3 CONC CENT PRODUCT PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-013-CON-CON-0270 | MP3B-#4 CONC CENT PRODUCT PUMP | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | DELETE |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
MEM-PRO-013-PKG-PAK-2214 | MP3B-PACKER NUIS DUST COLL ASP FAN | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | NOT ACCESSABLE |  |  | Never |  |  |  | 0 | #VALUE! | bar: WR to NR
MEM-PRO-010-MDU-AEQ-6815 | MMDU-INLET FILTER FOR COOLING RING AIR | [5 empty] | NR | NR | OK | OK | OK | [21 empty] | ???? |  |  | Never |  |  |  | 16 | #VALUE! | bar: WR to NR
init
pip
pok
rts
sch
MEM-PRO-010-UTL-PRW-6557 | MSS-140 DEG WTR TK NORTH PUMP | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
MEM-PRO-013-BGY-FCS-6295 | MP3B-N 600 VAC CONDENSATE PUMP | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
MEM-PRO-011-WEI-WIS-4106 | MP1-540/545 RECEIVER | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 24 | bar: WR to NR
MEM-PRO-011-WEI-WIS-4112 | MP1-540/545 PRECONDITIONER | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-011-WEI-WIS-4123 | MP1-540/545 WET-IN GRINDER #1 | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
MEM-PRO-011-WEI-WIS-4118 | MP1-540/545 WET-IN TUBE DISCH PUMP | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
MEM-PRO-013-PKG-PAK-2234 | MP3-ONLINE REWORK BAG SP STAT BLOWER | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
MEM-PRO-013-PKG-PAK-2270 | MP3B-BB PACKER | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
MEM-PRO-022-STS-W8T-5008 | MSS-W 800T BIN DISCH ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-014-GRD-MFG-3033 | MSP - D. GRND SRG HPPR DSCH RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-014-GRD-MFG-3025 | MSP - SOUTH GRINDER FEED RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-013-FED-FED-3020 | MP3B-FEED DRYER VENT FILTER COLLECTOR | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-014-GRD-MFG-3012 | MSP - NORTH GRINDER FEED RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-014-WEI-WIS-3038 | MSP-DUST COLLECTOR #3 ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-014-GRD-MFG-3025 | MSP - SOUTH GRINDER FEED RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-014-GRD-MFG-3047 | MSP-S. DUST COLLECTOR DSCH RFV #2 | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-014-GRD-MFG-3012 | MSP - NORTH GRINDER FEED RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-014-GRD-MFG-3042 | MSP-N. DUST COLLECTOR DSCH RFV #1 | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-022-STS-E8T-5010 | MSS-E 800T BIN DISCH ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-014-SPR-PRC-5205 | MSP-DRY REWORK ASPIRATION BIN RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-011-PKG-PAK-5306 | MP1B-ASPIRATION FILTER RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-PKG-BLD-3699 | MSP-PACKAGING ASPIRATION FILTER RCVR RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3647 | MSP-DRYER BOTTOM PRODUCT SCREENER RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3690 | MSP-SW CYCLONE ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3635 | MSP-SW FILTER ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3686 | MSP-SE CYCLONE ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3619 | MSP-SE FILTER ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-PRC-3650 | MSP-PRODUCT COLLECTOR RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3692 | MSP-NW CYCLONE ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3643 | MSP-NW FILTER ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3688 | MSP-NE CYCLONE ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-DRY-3628 | MSP-NE FILTER ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-SPR-PRC-3644 | MSP-MAIN DRYER BODY RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-FED-FED-3831 | MSP-WEST CYCLONE DISCH RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-FED-FED-3823 | MSP-FEED DRYER SURGE BIN DISCH RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-FED-FED-3837 | MSP-FEED DRYER DRY FEED RECVR DISCH RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-FED-FED-3825 | MSP-SURGE BIN DISC RFV TO FEED LOADOUT | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-FED-FED-3804 | MSP-BED DRYER #1 & #2 DISCH ROTARY VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-014-FED-FED-3865 | MSP-FEED DRYER BAGHOUSE DISC RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8109 | MS2P-VF BAGHOUSE RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8063 | MS2P-NW BAGHOUSE RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8041 | MS2P-SE CSP CYCLONE FINES RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8083 | MS2P-SE BAGHOUSE RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8073 | MS2P-SW BAGHOUSE RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8037 | MS2P-SW CMC CYCLONE RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8040 | MS2P-SE CMC CYCLONE RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8035 | MS2P-NW CSP CYCLONE FINES RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8038 | MS2P-SW CSP CYCLONE FINES RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8034 | MS2P-NW CMC CYCLONE RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8031 | MS2P-NE CMC CYCLONE RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8053 | MS2P-NE BAGHOUSE RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-015-SPR-DRY-8032 | MS2P-NE CSP CYCLONE FINES RFV | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 32 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 32 | bar: WR to NR
MEM-PRO-013-PCP-PHA-0080 | MP3B-CLARIFIED TANK | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
MEM-PRO-011-UTL-PWS-5538 | CITY WATER BOOSTER PUMP | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-011-MEB-CLF-5508 | ALPHA CLARIFIER TANK PUMP | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 32 | bar: WR to NR
MEM-PRO-011-MEB-FCS-5832 | MP1 FLASH COOLER DISCH PUMP | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 32 | bar: WR to NR
MEM-PRO-010-SLM-AEQ-5827 | MS2P-ACID LINE BLEED VALVE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 32 | bar: WR to NR
MEM-PRO-010-SLM-AEQ-5912 | MS2P-SLAM CONDENSATE PUMP | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-011-MEB-MES-5926 | MP1 ALPHA RECIRC. PUMP # 2 | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-011-MEB-MES-5928 | MP1 ALPHA RECIRC. PUMP # 3 | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-011-MEB-MES-5942 | MP1 ALPHA RECIRC. PUMP # 4 | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-011-MEB-MES-5945 | MP1 ALPHA RECIRC. PUMP # 5 | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
[7 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-011-MEB-CLF-5516 | ALPHA CLARIFIER CENTRIFUGE | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 0 | bar: WR to NR
MEM-PRO-011-MEB-MES-5902 | MP1 ALPHA ULTRA FILTRATION FEED PUMP | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 24 | bar: WR to NR
MEM-PRO-011-MEB-MES-5909 | MP1 ALPHA CIP PUMP FROM BALANCE TANK | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 24 | bar: WR to NR
MEM-PRO-010-MDU-AEQ-7025 | MMDU-ASP. DCE GROUND FLAKE COLLECTOR | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
MEM-PRO-010-MDU-AEQ-7035 | MMDU-U-42" WHOLE FLAKE GRINDER | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 16 | bar: WR to NR
MEM-PRO-010-UTL-CWS-8510 | MSS-WEST PROCESS COOLING TOWER | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
MEM-PRO-010-UTL-CWS-8520 | MSS-EAST UTILITY COOLING TOWER | [5 empty] | NR | OK | OK | OK | OK | [24 empty] | #N/A |  |  |  | 8 | bar: WR to NR
Formulas:
Last Reading = VLOOKUP([New Number],'[10]Monthly AMS report'!HR$1:HS1048576,2,FALSE())
Last Reading = VLOOKUP([New Number],'[10]Monthly AMS report'!EB$1:EC1048576,2,FALSE())